## DMSMatchingTemplateInfo (hidden)
YesNo | TrueFalse | AlarmEventCause | AlarmSeverity | MeasurementType | UnitsType | AbnormalState | TagSemantics | DMSType | DiscreteSignalType | CommAlarmSetCategory | RemoteUnitAlarmType | PhaseCode | WindingType | SignalDirection | AnalogSignalType | UnitSymbol | FlowDirection | RemoteUnitType | TimeZone | RedundancyBehaviorType | ConnectionModeType | ProtocolTypeConitel | SOEGroup | ScanTypeConitel | RemotePointType | OperateType | DiscreteInputTypeConitel | SectionConitel | DiscreteOutputDataTypeConitel | CommandTypeConitel | FunctionCodeConitel | AnalogInputTypeConitel | DeadbandDataType | DNP3Scan | TimeSyncMode | DNP3ConfirmMode | DNP3LinkStatusCommand | IpVersion | DNP3ObjectGroup | DNP3InputType | DNP3OutputType | ControlCode | DNP3Variation | DNP3CounterType | DNP3SlaveEvent | DNP3SlaveDiscreteInputDataType | DNP3SlaveClassData | DNP3SlaveAnalogInputDataType | DNP3SlaveCounterDataType | IccpVersion | IccpBlocks | ConnectionRole | ServiceRole | AuthenticationMode | DstsType | IccpScope | IccpDataValueType | IECCounterInterrogationType | IECClockSyncMode | OctetSize | IEC101LinkMode | IEC101ConfirmMode | ModemCallType | ModemCommandType | BaudRate | IECInterrogationType | IECInterrogationGroup | IECDiscreteType | IECCommandQualifier | CommandState | IECAnalogType | IECRateType | ScanTypeMD3 | DiscreteInputModuleTypeMD3 | DiscreteInputDataTypeMD3 | DiscreteOutputTypeMD3 | DiscreteOutputDataTypeMD3 | CmdTypeMD3 | AnalogInputModuleTypeMD3 | AnalogInputDataTypeMD3 | AnalogOutputTypeMD3 | ModbusByteOrder | ModbusTransmissionMode | ModbusRegisterType | ModbusDiscreteOutputType | ModbusAnalogType | SecurityCodeSeries5 | ScanTypeSeries5 | DiscreteTypeSeries5 | ScanTypeVanComm | DiscreteInputTypeVanComm | DiscreteOutputTypeVanComm | AnalogTypeVanComm | RTUMode2179 | AnalogFormat2179 | DiscreteFormat2179 | ObjectType2179 | ControlCodePGE2179 | ControlState2179 | DiscreteInputType2179 | DiscreteOutputType2179 | DERStatusAttributeType | MQTTProtocolVersion | MQTTQoSLevel | MQTTPayloadFormat | MQTTDataType | MQTTTopicType | CalculationParamType | InputTriggerType | RemoteUnitType | RedundancyBehaviorType | RemotePointType | OperateType | RemotePointType | OperateType | RemotePointType | MeasurementType | OperateType | RemotePointType | OperateType | DNP3InputType | RemotePointType | OperateType | RemotePointType | OperateType | MeasurementType | RemotePointType | OperateType | DNP3SlaveDiscreteInputDataType | DNP3SlaveDiscreteInputDataType | RemotePointType | OperateType | RemoteUnitType | RedundancyBehaviorType | RemoteUnitType | RemotePointType | IccpDataValueType | OperateType | RemotePointType | IccpDataValueType | OperateType | RemotePointType | IccpDataValueType | MeasurementType | OperateType | IccpDataValueType | OperateType | IccpDataValueType | OperateType | RemoteUnitType | RemotePointType | OperateType | RemotePointType | IECAnalogType | OperateType | RemotePointType | MeasurementType | IECAnalogType | OperateType | RemotePointType | IECDiscreteType | IECDiscreteType | OperateType | RemotePointType | IECAnalogType | OperateType | RemoteUnitType | RedundancyBehaviorType | OctetSize | RemoteUnitType | RemotePointType | IECDiscreteType | IECDiscreteType | OperateType | RemotePointType | IECAnalogType | IECAnalogType | OperateType | RemotePointType | IECAnalogType | IECAnalogType | MeasurementType | OperateType | RedundancyBehaviorType | RemotePointType | OperateType | RemotePointType | OperateType | RemotePointType | MeasurementType | OperateType | RedundancyBehaviorType | RemotePointType | OperateType | RemotePointType | ModbusRegisterType | OperateType | RemotePointType | ModbusRegisterType | MeasurementType | OperateType | RedundancyBehaviorType | RemotePointType | OperateType | RemotePointType | OperateType | RemotePointType | MeasurementType | OperateType | RedundancyBehaviorType | RemotePointType | OperateType | RemotePointType | OperateType | RemotePointType | MeasurementType | OperateType | RemotePointType | RemotePointType | RemotePointType | MeasurementType | RemotePointType | RemotePointType | IECDiscreteType | IECDiscreteType | OperateType | RemotePointType | IECAnalogType | OperateType | CalculationParamType
No | TRUE | Application Alarm | Trivial | Unitless | Absolute | Normal | Do Not Operator Close | Substation | Custom | Remote Unit | Comm Failure On All Links | Unknown | None | Read | Custom | Default | Undirected | RTU | (UTC-12:00) International Date Line West | Prioritize Cost Factor | Normal | Conitel 2025 | Group 0-7 | Scan | Analog | Direct | Single Bit | Section A | Single Coordinate | Trip/Close | Trip | 12-bit signed magnitude | Int32 | Class 0 | LAN | Never | Request Link Status | IP version 4 | Binary Input | Single-Bit | Single-Coord | Nul | Unspecified | Undefined | Without Time | Binary Input Packed Format | Class 1 | Int32 With Flag | Int32 With Flag | 1996 | Block 1 | Outgoing | Client | None | Manual RBE | VCC | Unknown | Counter Read | Clock sync | 1 | Unbalanced | Sometimes | Dial-Out | Baud Rate | 100 | Interrogation | General | No Input | Default | On/Higher | Short Normalized | Rate with Timestamp | Analog Unconditional | Digital Input Module DCM | Single Bit | Raise-Lower | Single Coordinate | Trip | Analog Input Module | 12-bit signed magnitude | AOM Type | Little Endian | TCP | Coil | Single-Coord | Short | LRC 8-bit | Exception | Single-Coord | Analog Scan | Momentary Status | Single-Coord | 12-bit Signed | Normal Mode | 13-bit | 1-bit | Discrete | Pulse | Open | Single-Bit | Single-Coord | Alarm Status | 3.1.1 | At Most Once (QoS 0) | ASCII | Int8 | Online | Bool | None | RTU | Prioritize Cost Factor | Discrete | Direct | Analog | Direct | Analog | Discrete | Direct | Discrete | Direct | Single-Bit | Analog | Direct | Analog | Direct | Discrete | Discrete | Direct | Binary Input Packed Format | Binary Input Packed Format | Analog | Direct | Control Center | Prioritize Cost Factor | Control Center | Discrete | State | Direct | Analog | Real | Direct | Analog | Real | Discrete | Direct | State | Direct | Real | Direct | RTU | Discrete | Direct | Analog | Short Normalized | Direct | Analog | Discrete | Short Normalized | Direct | Discrete | Single-Bit | Single-Bit | Direct | Analog | Short Normalized | Direct | RTU | Prioritize Cost Factor | 1 | RTU | Discrete | Single-Bit | Single-Bit | Direct | Analog | Short Normalized | Short Normalized | Direct | Analog | Short Normalized | Short Normalized | Discrete | Direct | Prioritize Cost Factor | Discrete | Direct | Analog | Direct | Analog | Discrete | Direct | Prioritize Cost Factor | Discrete | Direct | Analog | Coil | Direct | Analog | Coil | Discrete | Direct | Prioritize Cost Factor | Discrete | Direct | Analog | Direct | Analog | Discrete | Direct | Prioritize Cost Factor | Discrete | Direct | Analog | Direct | Analog | Discrete | Direct | Discrete | Analog | Analog | Discrete | Analog | Discrete | Single-Bit | Single-Bit | Direct | Analog | Short Normalized | Direct | Bool
Yes | FALSE | Discrete State | Low | Voltage | Relative | Abnormal | Do Not Operator Open | Bay | Switch Status | Communication Link | Comm Failure On All Links RTN | N | Primary | Write | Measured Value | kV | Forward | Substation Control System | (UTC-11:00) Coordinated Universal Time-11 | Switch On First RTU Failure | Lab | Baker | Group 8-F | SOE Scan | Discrete | Select With Value | Single-Bit MCD-A | Section B | Two Coordinates | Raise/Lower | Close | 12-bit signed 2's complement | Int16 | Class 0123 | Serial | Sometimes | Reset Link | IP version 6 | Binary Input Event | Double-Bit | Multi-Coord | Pulse On | Int32 | Counter | With Absolute Time | Binary Input With Flags | Class 2 | Int16 With Flag | Int16 With Flag | 2000 | Block 2 | Incoming | Server | MACE | Manual Interval | ICC | Real | Counter Freeze with Reset | Clock sync with configured delay | 2 | Balanced | Always | Dial-In | Phone No | 200 | Counter Interrogation | Group 1 | Single-Bit | Short Pulse | Off/Lower | Short Scaled | Rate with Short Timestamp | Analog Delta Scan | Digital Input Module | Multi-Bit | POM Type | Two Coordinates | Close | Floating Point Module | 12-bit signed 2's complement | Input Point Control | Big Endian | ASCII | Discrete Input | Two-Coord | UShort | CRC 16-bit | Status Scan | Two-Coord | All Status Scan | Memory Status | Two-Coord | 12-bit Unsigned | Virtual Mode | 16-bit | 2-bit | Analog | Bistable | Close | Multi-Coord | Multi-Coord | Get Connect Status |  | At Least Once (QoS 1) | Sparkplug | Int16 | Offline | Int | Value | Terminal Server | Switch On First RTU Failure |  | Automatic With Value | Counter | Automatic With Value | Counter |  | Automatic With Value |  | Automatic With Value | Double-Bit | Counter | Automatic With Value | Counter | Automatic With Value |  |  | Automatic With Value | Binary Input With Flags | Binary Input With Flags | Counter | Automatic With Value | Data Set Transfer Set | Switch On First RTU Failure | Data Set Transfer Set |  | Discrete | Automatic With Value |  | Real Quality | Automatic With Value |  | Real Quality |  | Automatic With Value | Discrete | Automatic With Value | Real Quality | Automatic With Value | Modem Bank |  | Automatic With Value | Counter | Short Scaled | Automatic With Value | Counter |  | Short Scaled | Automatic With Value |  | Double-Bit | Double-Bit | Automatic With Value | Counter | Short Scaled | Automatic With Value |  | Switch On First RTU Failure | 2 |  |  | Double-Bit | Double-Bit | Automatic With Value | Counter | Short Scaled | Short Scaled | Automatic With Value | Counter | Short Scaled | Short Scaled |  | Automatic With Value | Switch On First RTU Failure |  | Automatic With Value | Counter | Automatic With Value | Counter |  | Automatic With Value | Switch On First RTU Failure |  | Automatic With Value | Counter | Holding Register | Automatic With Value | Counter | Holding Register |  | Automatic With Value | Switch On First RTU Failure |  | Automatic With Value | Counter | Automatic With Value | Counter |  | Automatic With Value | Switch On First RTU Failure |  | Automatic With Value | Counter | Automatic With Value | Counter |  | Automatic With Value |  | Counter | Counter |  |  |  | Double-Bit | Double-Bit | Automatic With Value | Counter | Short Scaled | Automatic With Value | Int
|  | Analog High | Minor | Current |  | Auto | Do Not Auto Close | Base Voltage | Local/remote |  | DNP3 IIN Alarm | C | Secondary | Read-Write | Setpoint | V | Reverse | Control Center | (UTC-10:00) Aleutian Islands | Switch On All RTU Failure |  |  |  |  | Counter | Select Without Value | Multi-Bit |  | Multi Coordinates |  | Raise | 6-bit unsigned | Float | Scan Table |  | Always |  |  | Double Binary Input | Multi-Coord |  | Pulse Off | Int16 | Frozen Counter | With Relative Time | Double-bit Binary Input Packed Format | Class 3 | Int32 Without Flag | Int32 Without Flag |  | Block 3 |  | Peer | SSL | Auto All |  | State | Counter Freeze without Reset | Clock sync with measured delay | 3 |  | Never |  | Command | 300 |  | Group 2 | Double-Bit | Long Pulse |  | Float | Rate | Digital COS/Time Tagged |  | Multi-Bit BCD | DOM Type | Multi Coordinates | Raise | Analog Input Module DCM | 12-bit unsigned | Floating Point O/P Command |  | RTU | Input Register | Multi-Coord | Int32 |  | Analog Scan | Multi-Coord | Momentary Status Scan | Latching Status | Multi-Coord |  |  |  |  | Accumulator |  |  |  |  | Inverter Status |  | Exactly Once (QoS 2) |  | Int32 | Data | Double | Flags |  | Switch On All RTU Failure | [8 empty] | Direct No Ack | Multi-Coord |  | Direct No Ack |  | Direct No Ack |  |  | Direct No Ack | Double-bit Binary Input Packed Format | Double-bit Binary Input Packed Format |  | Direct No Ack |  | Switch On All RTU Failure |  |  | State Supplement |  |  | Real Quality TimeTag |  |  | Real Quality TimeTag |  |  | State Supplement |  | Real Quality TimeTag |  | Terminal Server |  |  |  | Float |  |  |  | Float |  |  | Position | Position |  |  | Float | Direct No Ack |  | Switch On All RTU Failure |  |  |  | Position | Position |  |  | Float | Float |  |  | Float | Float |  |  | Switch On All RTU Failure | [7 empty] | Switch On All RTU Failure | [9 empty] | Switch On All RTU Failure | [7 empty] | Switch On All RTU Failure | [13 empty] | Position | Position |  |  | Float | Direct No Ack | Double
|  | Analog Low | Medium | Active Power |  |  | Do Not Auto Open | Network | Operation Count |  | DNP3 IIN Event | CN | Tertiary |  | Bandwidth | mV |  | IED | (UTC-10:00) Hawaii | Cost Factor With Availability Check |  |  |  |  | Smart Meter | Automatic With Value | Multi-Bit BCD |  |  |  | Lower | 12-bit unsigned | [6 empty] | Double Binary Input Event | Multi-Coord BCD |  | Latch On | Float |  |  | Double-bit Binary Input With Flags | None | Int16 Without Flag | Int16 Without Flag |  | Block 4 |  |  |  | Auto Real |  | Discrete | Counter Reset |  | Undefined |  |  |  | Delay | 600 |  | Group 3 | Position | Persistent |  | Short Normalized + Timestamp |  | Digital Unconditional |  |  | Input Point Control |  | Lower |  | Floating Point |  |  |  | Holding Register |  | UInt32 |  | Setpoint Scan |  | Memory Status Scan | MultiBit | Raise/Lower |  |  |  |  | Analog Output |  |  |  |  | Local Control Mode Status |  |  |  | Int64 | Command | String | Timestamp | [19 empty] | Double-bit Binary Input With Flags | Double-bit Binary Input With Flags | [6 empty] | State Quality |  |  | Real Extended |  |  | Real Extended |  |  | State Quality |  | Real Extended | [5 empty] | Short Normalized + Timestamp |  |  |  | Short Normalized + Timestamp |  |  | Bitstring | Bitstring | [9 empty] | Bitstring | Bitstring |  |  | Short Normalized + Timestamp | Short Normalized + Timestamp |  |  | Short Normalized + Timestamp | Short Normalized + Timestamp | [42 empty] | Bitstring | Bitstring |  |  |  |  | String
|  | Analog Creep | Major | Reactive Power |  |  | Warn On Open | Fault Indicator Catalog | Tap Position |  | DNP3 Response To IIN Failed | B |  |  | Control Delay | A |  | Smart Meter | (UTC-09:30) Marquesas Islands | [5 empty] | Array | Automatic | Single-Bit MCD-B |  |  |  |  | Remote status byte | [6 empty] | Binary Output |  |  | Latch Off | Double |  |  | Multi-bit Binary Input Packed Format |  | Float With Flag |  |  | Block 5 |  |  |  | Auto Discrete |  | State Supplement | [7 empty] | 1200 |  | Group 4 | Bitstring |  |  | Short Scaled + Timestamp |  | Floating Point Unconditional |  |  |  |  | Point Off |  | 15-bit signed magnitude |  |  |  | Output Coil |  | Float |  |  |  | Latching Status Scan | [6 empty] | Discrete Output |  |  |  |  | Manufacturer Status |  |  |  | UInt8 |  | Analog Signal | AlarmLimit | [27 empty] | Discrete Quality |  |  | Real Quality Extended |  |  | Real Quality Extended |  |  | Discrete Quality |  | Real Quality Extended | [5 empty] | Short Scaled + Timestamp |  |  |  | Short Scaled + Timestamp |  |  | Multibit | Multibit | [9 empty] | Multibit | Multibit |  |  | Short Scaled + Timestamp | Short Scaled + Timestamp |  |  | Short Scaled + Timestamp | Short Scaled + Timestamp | [42 empty] | Multibit | Multibit |  |  |  |  | Analog Signal
|  | Analog Growth Rate | High | Power Factor |  |  | Warn On Close | 2-Winding Transformer Catalog | Tap Raise/Lower |  | DNP3 Secure Auth Threshold | BN |  |  | Subsequent Delay | kA |  | Modem Bank | (UTC-09:00) Alaska | [6 empty] | Direct No Ack | Single-Bit MCD-C | [11 empty] | Binary Output Event |  |  | Close/Pulse-On |  |  |  | Multi-bit Binary Input With Flags |  | Double With Flag | [6 empty] | Auto State |  | Real Quality | [7 empty] | 2400 |  | Group 5 | Multibit |  |  | Float + Timestamp |  | Floating Point Delta |  |  |  |  | Point On |  | 15-bit signed 2's complement |  |  |  | Output Holding Register | [5 empty] | Status Exception Scan | [11 empty] | Operational Mode Status |  |  |  | UInt16 |  | Discrete Signal | [28 empty] | State Supplement Quality | [8 empty] | State Supplement Quality | [7 empty] | Float + Timestamp |  |  |  | Float + Timestamp |  |  | Single-Bit + Timestamp | [10 empty] | Single-Bit + Timestamp | Single-Bit + Timestamp |  |  | Float + Timestamp | Float + Timestamp |  |  | Float + Timestamp | Float + Timestamp | [42 empty] | Single-Bit + Timestamp | [5 empty] | Discrete Signal
|  | Analog Flatline | Critical | Frequency |  |  | Predicted | 3-Winding Transformer Catalog | Enabled |  | DNP3 Secure Comm Threshold | BC |  |  | High Limit | mA |  | Data Set Transfer Set | (UTC-09:00) Coordinated Universal Time-09 | [7 empty] | Double-Bit MCD-A | [11 empty] | Binary Counter |  |  | Trip/Pulse-On | [14 empty] | State Quality | [7 empty] | 4800 |  | Group 6 | Single-Bit + Timestamp |  |  | Short Normalized (No Quality) |  | Floating Point COS/Time-Tagged |  |  |  |  | Single Pole Operate |  | 15-bit unsigned |  |  |  | Output Mask Holding Register | [5 empty] | Read Internal Status | [11 empty] | State of Charge Status |  |  |  | UInt32 |  | BoolArray | [28 empty] | State Quality TimeTag | [8 empty] | State Quality TimeTag | [7 empty] | Short Normalized (No Quality) |  |  |  | Short Normalized (No Quality) |  |  | Double-Bit + Timestamp | [10 empty] | Double-Bit + Timestamp | Double-Bit + Timestamp |  |  | Short Normalized (No Quality) | Short Normalized (No Quality) |  |  | Short Normalized (No Quality) | Short Normalized (No Quality) | [42 empty] | Double-Bit + Timestamp | [5 empty] | Analog Signal Array
|  | Analog Drop Rate |  | Temperature |  |  | Confirmed | Synchronous Machine Catalog | Load Bonus |  | DNP3 Secure Threshold RTN | BCN |  |  | Low Limit | kW |  | Terminal Server | (UTC-08:00) Baja California | [7 empty] | Double-Bit MCD-B | [11 empty] | Frozen Counter |  |  | Close/Pulse-Off | [14 empty] | Discrete Quality | [7 empty] | 9600 |  | Group 7 | Double-Bit + Timestamp |  |  | Short Normalized + Short Timestamp | [6 empty] | Custom (Payload 0) | [5 empty] | Multiple Holding Registers | [5 empty] | Clear Internal Status | [11 empty] | Storage Mode Status |  |  |  | UInt64 |  | IntArray | [28 empty] | Discrete Quality TimeTag | [8 empty] | Discrete Quality TimeTag | [7 empty] | Short Normalized + Short Timestamp |  |  |  | Short Normalized + Short Timestamp |  |  | Position + Timestamp | [10 empty] | Position + Timestamp | Position + Timestamp | [50 empty] | Position + Timestamp | [5 empty] | Discrete Signal Array
|  | Analog Return-to-Normal |  | Active Energy |  |  | Out Of Order | Capacitor Catalog | Reclosing Enabled |  | Event Buffer Overflow | A |  |  | Real Compensation | MW |  | Report Control Block | (UTC-08:00) Coordinated Universal Time-08 | [7 empty] | Double-Bit MCD-C | [11 empty] | Counter Event |  |  | Trip/Pulse-Off | [14 empty] | State Supplement Quality | [7 empty] | 19200 |  | Group 8 | Position + Timestamp |  |  | Short Scaled + Short Timestamp | [6 empty] | Custom (Payload 1) | [11 empty] | Status Acknowledge | [11 empty] | Stor Connect Status |  |  |  | Float |  | DoubleArray | [28 empty] | State Supplement Quality TimeTag | [8 empty] | State Supplement Quality TimeTag | [7 empty] | Short Scaled + Short Timestamp |  |  |  | Short Scaled + Short Timestamp |  |  | Bitstring + Timestamp | [10 empty] | Bitstring + Timestamp | Bitstring + Timestamp | [50 empty] | Bitstring + Timestamp
|  | Transformer Overload |  | Reactive Energy |  |  | Malfunctioning | Petersen Coil Catalog | Active Setting |  | File Transfer Failed | AN |  |  | Imaginary Compensation | W |  | SubRTU | (UTC-08:00) Pacific Time (US & Canada) | [19 empty] | Frozen Counter Event |  |  | Close/Latch-On | [14 empty] | Real Quality TimeTag | [7 empty] | 38400 |  | Group 9 | Bitstring + Timestamp |  |  | Float + Short Timestamp | [6 empty] | Custom (Payload 32) | [23 empty] | Custom Status Attribute 1 |  |  |  | Boolean |  | StringArray | [28 empty] | State Extended | [8 empty] | State Extended | [7 empty] | Float + Short Timestamp |  |  |  | Float + Short Timestamp |  |  | Multibit Timestamp | [10 empty] | Multibit Timestamp | Multibit Timestamp | [50 empty] | Multibit Timestamp
|  | Line Overload |  | Apparent Power |  |  | Alarm Inhibit | Joint Catalog | Refresh |  | ICCP Block 4 Plugin Failure | AC |  |  | Fault Recorder | kVAr |  |  | (UTC-07:00) Arizona | [19 empty] | Analog Input |  |  | Trip/Latch-On | [14 empty] | State Quality TimeTag | [7 empty] | 56000 |  | Group 10 | Multibit Timestamp | [33 empty] | Custom Status Attribute 2 | [5 empty] | Analog Signal Array | [28 empty] | Discrete Extended | [8 empty] | Discrete Extended | [14 empty] | Single-Bit + Short Timestamp | [62 empty] | Single-Bit + Short Timestamp
|  | Analog Reasonability |  | Voltage Angle |  |  | Alarm Audio Inhibit | Disconnector Catalog | Voltage Index (Primary) |  | Init Sequence Failed | ACN |  |  | Weather Data | MVAr |  |  | (UTC-07:00) La Paz, Mazatlan | [19 empty] | Frozen Analog Input |  |  | Close/Latch-Off | [14 empty] | Discrete Quality TimeTag | [7 empty] | 64000 |  | Group 11 | Single-Bit + Short Timestamp | [33 empty] | Custom Status Attribute 3 | [5 empty] | Discrete Signal Array | [28 empty] | State Supplement Extended | [8 empty] | State Supplement Extended | [14 empty] | Double-Bit + Short Timestamp | [62 empty] | Double-Bit + Short Timestamp
|  | System Alarm |  | Status |  |  | Stop Processing | Sectionalizer Catalog | Voltage Index (Secondary) |  | Init Seq Partially Succeeded | AB |  |  | Bellwether Meter | VAr |  |  | (UTC-07:00) Mountain Time (US & Canada) | [19 empty] | Analog Input Event |  |  | Trip/Latch-Off | [14 empty] | State Supplement Quality TimeTag | [9 empty] | Group 12 | Double-Bit + Short Timestamp | [68 empty] | State Quality Extended | [8 empty] | State Quality Extended | [14 empty] | Position + Short Timestamp | [62 empty] | Position + Short Timestamp
|  | DOM Alarm |  | Discrete |  |  | Point Test | Load Breaker Catalog | Load Flow Enabled |  | Invalid Timestamp | ABN |  |  | Reclose Delay | Hz |  |  | (UTC-07:00) Yukon | [19 empty] | Frozen Analog Input Event | [17 empty] | Real Extended | [9 empty] | Group 13 | Position + Short Timestamp | [68 empty] | Discrete Quality Extended | [8 empty] | Discrete Quality Extended | [14 empty] | Bitstring + Short Timestamp | [62 empty] | Bitstring + Short Timestamp
|  | Remote Unit Alarm |  | Switch Status |  |  | DOM Inhibit | Fuse Catalog | Fault Status |  | Missing IOA | ABC |  |  | Subtransient Fault Current | Hz/s |  |  | (UTC-06:00) Central America | [19 empty] | Analog Output Status | [17 empty] | State Extended | [9 empty] | Group 14 | Bitstring + Short Timestamp | [68 empty] | State Supplement Quality Extended | [8 empty] | State Supplement Quality Extended | [14 empty] | Multibit Short Timestamp | [62 empty] | Multibit Short Timestamp
|  | Communication Link Alarm |  | Time |  |  |  | Circuit Breaker Catalog | Recloser Lockout |  | Modem Activate Link Failed | ABCN |  |  | Subtransient Fault Angle | C |  |  | (UTC-06:00) Central Time (US & Canada) | [19 empty] | Analog Output Event | [17 empty] | Discrete Extended | [9 empty] | Group 15 | Multibit Short Timestamp
|  |  |  | Humidity |  |  |  | Connectivity Node | Fan Status |  | Modem Availability Timed Out |  |  |  | Transient Fault Current | F |  |  | (UTC-06:00) Easter Island | [19 empty] | Class Objects | [17 empty] | State Supplement Extended | [9 empty] | Group 16
|  |  |  | Wind Speed |  |  |  | Bus Node | Oil Pump Status |  | Modem Call Timed Out |  |  |  | Transient Fault Angle | kWh |  |  | (UTC-06:00) Guadalajara, Mexico City, Monterrey | [19 empty] | Authentication | [17 empty] | Real Quality Extended | [9 empty] | Cyclic
|  |  |  | Feels Like |  |  |  | Potential Transformer | Hotline Tag |  | Periodic Command Failed |  |  |  | Delta Voltage | MWh |  |  | (UTC-06:00) Saskatchewan | [19 empty] | Secure DNP3 Statistics | [17 empty] | State Quality Extended
|  |  |  | Sunshine Minutes |  |  |  | Surge Protector | Max. Operation Count |  | Periodic Command Timed Out |  |  |  | Maximum Ramp Up | kVArh |  |  | (UTC-05:00) Bogota, Lima, Quito, Rio Branco | [19 empty] | Secure DNP3 Statistics Event | [17 empty] | Discrete Quality Extended
|  |  |  | Sky Cover |  |  |  | Ground Impedance | Hourly Operation Count |  | PG&E Normal RTU Point Count Mismatch |  |  |  | Maximum Ramp Down | MVArh |  |  | (UTC-05:00) Chetumal | [37 empty] | State Supplement Quality Extended
|  |  |  | Length |  |  |  | Equivalent Load | Daily Operation Count |  | PG&E Virtual RTU Point Count Mismatch |  |  |  | Charged | kVA |  |  | (UTC-05:00) Eastern Time (US & Canada)
|  |  |  | Cross-section |  |  |  | Supply Line | Monthly Operation Count |  | Protocol Invalid Timestamp |  |  |  | Energy Price | MVA |  |  | (UTC-05:00) Haiti
|  |  |  | Impedance |  |  |  | Capacitor | Under-Frequency Alarm |  | Remote Status Indication Alarm |  |  |  | Generation Price | VA |  |  | (UTC-05:00) Havana
|  |  |  | Admittance |  |  |  | Synchronous Machine | Forward |  | Remote Status Indication Event |  |  |  | P Injected Real | Degree |  |  | (UTC-05:00) Indiana (East)
|  |  |  | Impedance per Length |  |  |  | Current Transformer | Relay Trip |  | Telemetry Failure Init Sequence |  |  |  | Q Injected Real | Dms |  |  | (UTC-05:00) Turks and Caicos
|  |  |  | Admittance per Length |  |  |  | Series Compensator | Reverse Mode |  | Telemetry Failure Periodic Cmd |  |  |  | P Injected Equivalent | s |  |  | (UTC-04:00) Atlantic Time (Canada)
|  |  |  | Percent |  |  |  | Fault Indicator | Source Status |  | Telemetry Failure RTN |  |  |  | Q Injected Equivalent | min |  |  | (UTC-04:00) Caracas
|  |  |  | Money |  |  |  | Line | Parallel |  | Unknown Input Coordinate |  |  |  | Calculated Voltage | hour |  |  | (UTC-04:00) Cuiaba
|  |  |  | Relative Voltage |  |  |  | Tap Changer | Power On |  | Invalid Field Time Replacement |  |  |  | P Min | km/h |  |  | (UTC-04:00) Georgetown, La Paz, Manaus, San Juan
|  |  |  | Irradiation |  |  |  | 2-Winding Transformer | Manageable | [5 empty] | P Max | mph |  |  | (UTC-04:00) Santiago
|  |  |  | Current Angle |  |  |  | 3-Winding Transformer | Malfunctioning | [5 empty] | Q Min | m/s |  |  | (UTC-03:30) Newfoundland
|  |  |  | Rotation Speed |  |  |  | Analog Signal | Weighting Factor | [5 empty] | Q Max | m |  |  | (UTC-03:00) Araguaina
|  |  |  | Mass |  |  |  | Discrete Signal | Temporary Fault Status | [5 empty] | S Short Circuit | km |  |  | (UTC-03:00) Asuncion
|  |  |  | Failure Rate |  |  |  | Ground Node | Group Status | [5 empty] | X/R Ratio | ft |  |  | (UTC-03:00) Brasilia
|  |  |  | Soil Temperature |  |  |  | Remote Point | Alarm Status | [5 empty] | R Ward | yd |  |  | (UTC-03:00) Cayenne, Fortaleza
|  |  |  | Oil Temperature |  |  |  | Curve | Control Area Mode | [5 empty] | X Ward | mi |  |  | (UTC-03:00) City of Buenos Aires
|  |  |  | Hotspot Temperature |  |  |  | Petersen Coil | Phase Downstream | [5 empty] | R1 Short Circuit | mm² |  |  | (UTC-03:00) Montevideo
|  |  |  | Date/time |  |  |  | Composite Switch | Phase Upstream | [5 empty] | X1 Short Circuit | kcmil |  |  | (UTC-03:00) Punta Arenas
|  |  |  | Coordinates |  |  |  | Rack | Ground Downstream | [5 empty] | R2 Short Circuit | AWG |  |  | (UTC-03:00) Saint Pierre and Miquelon
|  |  |  | Date |  |  |  | Regulator | Ground Upstream | [5 empty] | X2 Short Circuit | Ohm |  |  | (UTC-03:00) Salvador
|  |  |  | Long-Distance Length |  |  |  | Control Limit | [6 empty] | R0 Short Circuit | S |  |  | (UTC-02:00) Coordinated Universal Time-02
|  |  |  | Precipitation |  |  |  | Day Type | [6 empty] | X0 Short Circuit | mS |  |  | (UTC-02:00) Greenland
|  |  |  | Wind Direction |  |  |  | Season | [6 empty] | Virtual Tie Line | uS |  |  | (UTC-02:00) Mid-Atlantic - Old
|  |  |  | Thermal Power |  |  |  | Load Response Characteristics | [6 empty] | Time Multiplier | Ohm/km |  |  | (UTC-01:00) Azores
|  |  |  | Emission |  |  |  | Cold Load Pickup | [6 empty] | Minimum Response Time | Ohm/m |  |  | (UTC-01:00) Cabo Verde Is.
[8 empty] | Load Group | [6 empty] | Fault Resistance | Ohm/1000ft |  |  | (UTC) Coordinated Universal Time
[8 empty] | Sectionalizer | [6 empty] | Fault Reactance | Ohm/mi |  |  | (UTC+00:00) Dublin, Edinburgh, Lisbon, London
[8 empty] | Reclosing Stage | [6 empty] | Fault Distance | S/km |  |  | (UTC+00:00) Monrovia, Reykjavik
[8 empty] | Protection Equipment | [7 empty] | S/m |  |  | (UTC+00:00) Sao Tome
[8 empty] | Relay Stage | [7 empty] | S/1000ft |  |  | (UTC+01:00) Casablanca
[8 empty] | RTU Catalog | [7 empty] | S/mi |  |  | (UTC+01:00) Amsterdam, Berlin, Bern, Rome, Stockholm, Vienna
[8 empty] | Geographical Region | [7 empty] | μS/km |  |  | (UTC+01:00) Belgrade, Bratislava, Budapest, Ljubljana, Prague
[8 empty] | Geographical Subregion | [7 empty] | μS/m |  |  | (UTC+01:00) Brussels, Copenhagen, Madrid, Paris
[8 empty] | Feeder | [7 empty] | μS/1000ft |  |  | (UTC+01:00) Sarajevo, Skopje, Warsaw, Zagreb
[8 empty] | Feeder Object | [7 empty] | μS/mi |  |  | (UTC+01:00) West Central Africa
[8 empty] | Induction Machine | [7 empty] | % |  |  | (UTC+02:00) Athens, Bucharest
[8 empty] | Induction Machine Catalog | [7 empty] | Per Unit |  |  | (UTC+02:00) Beirut
[8 empty] | Wire Catalog | [7 empty] | V[120] |  |  | (UTC+02:00) Cairo
[8 empty] | Cable Catalog | [7 empty] | Currency |  |  | (UTC+02:00) Chisinau
[8 empty] | Line Geometry | [7 empty] | W/m² |  |  | (UTC+02:00) Gaza, Hebron
[8 empty] | Weather Region | [7 empty] | rpm |  |  | (UTC+02:00) Harare, Pretoria
[8 empty] | Transformer Area | [7 empty] | kg |  |  | (UTC+02:00) Helsinki, Kyiv, Riga, Sofia, Tallinn, Vilnius
[8 empty] | Customer Contract | [7 empty] | t |  |  | (UTC+02:00) Jerusalem
[8 empty] | Joint | [7 empty] | lb |  |  | (UTC+02:00) Juba
[8 empty] | Load Breaker | [7 empty] | 1/year |  |  | (UTC+02:00) Kaliningrad
[8 empty] | Circuit Breaker | [7 empty] | mm/h |  |  | (UTC+02:00) Khartoum
[8 empty] | Cable Thermal Model | [7 empty] | in/h |  |  | (UTC+02:00) Tripoli
[8 empty] | Array Signal | [7 empty] | MBTU/h |  |  | (UTC+02:00) Windhoek
[8 empty] | Interlocking Item | [7 empty] | kcal/h |  |  | (UTC+03:00) Amman
[8 empty] | Interlocking Scheme | [7 empty] | kJ/h |  |  | (UTC+03:00) Baghdad
[8 empty] | Control Settings | [7 empty] | MJ/h |  |  | (UTC+03:00) Damascus
[8 empty] | Feeder Segment | [7 empty] | 1000 hours |  |  | (UTC+03:00) Istanbul
[8 empty] | Fuse | [7 empty] | kg/h |  |  | (UTC+03:00) Kuwait, Riyadh
[8 empty] | Disconnector | [7 empty] | g/h |  |  | (UTC+03:00) Minsk
[8 empty] | Tag Catalog | [10 empty] | (UTC+03:00) Moscow, St. Petersburg
[8 empty] | Mobile Object | [10 empty] | (UTC+03:00) Nairobi
[8 empty] | AOR Group | [10 empty] | (UTC+03:00) Volgograd
[8 empty] | Custom Group | [10 empty] | (UTC+03:30) Tehran
[8 empty] | Interval Schedule | [10 empty] | (UTC+04:00) Abu Dhabi, Muscat
[8 empty] | Annual Schedule | [10 empty] | (UTC+04:00) Astrakhan, Ulyanovsk
[8 empty] | LV Network | [10 empty] | (UTC+04:00) Baku
[8 empty] | LV Feeder | [10 empty] | (UTC+04:00) Izhevsk, Samara
[8 empty] | Temperature-Dependent Schedule | [10 empty] | (UTC+04:00) Port Louis
[8 empty] | Current Transformer Catalog | [10 empty] | (UTC+04:00) Saratov
[8 empty] | Potential Transformer Catalog | [10 empty] | (UTC+04:00) Tbilisi
[8 empty] | Message Mapping | [10 empty] | (UTC+04:00) Yerevan
[8 empty] | Season Schedule | [10 empty] | (UTC+04:30) Kabul
[8 empty] | Custom Type | [10 empty] | (UTC+05:00) Ashgabat, Tashkent
[8 empty] | Generation Contract | [10 empty] | (UTC+05:00) Astana
[8 empty] | Distributed Generator | [10 empty] | (UTC+05:00) Ekaterinburg
[8 empty] | Power Plant | [10 empty] | (UTC+05:00) Islamabad, Karachi
[8 empty] | Customer | [10 empty] | (UTC+05:30) Chennai, Kolkata, Mumbai, New Delhi
[8 empty] | Service Location | [10 empty] | (UTC+05:30) Sri Jayawardenepura
[8 empty] | Busbar | [10 empty] | (UTC+05:45) Kathmandu
[8 empty] | Note Catalog | [10 empty] | (UTC+06:00) Bishkek
[8 empty] | Dynamic Line Rating | [10 empty] | (UTC+06:00) Dhaka
[8 empty] | Dynamic Transformer Rating | [10 empty] | (UTC+06:00) Omsk
[8 empty] | Relay Settings | [10 empty] | (UTC+06:30) Yangon (Rangoon)
[8 empty] | Distance Relay Settings | [10 empty] | (UTC+07:00) Bangkok, Hanoi, Jakarta
[8 empty] | Distance Relay Stage | [10 empty] | (UTC+07:00) Barnaul, Gorno-Altaysk
[8 empty] | Relay Condition | [10 empty] | (UTC+07:00) Hovd
[8 empty] | Regulator Group | [10 empty] | (UTC+07:00) Krasnoyarsk
[8 empty] | Transformer Bank | [10 empty] | (UTC+07:00) Novosibirsk
[8 empty] | Capacitor Bank | [10 empty] | (UTC+07:00) Tomsk
[8 empty] | Protection Group | [10 empty] | (UTC+08:00) Beijing, Chongqing, Hong Kong, Urumqi
[8 empty] | Transmission Network | [10 empty] | (UTC+08:00) Irkutsk
[8 empty] | Meter Catalog | [10 empty] | (UTC+08:00) Kuala Lumpur, Singapore
[8 empty] | 61850 Logical Node | [10 empty] | (UTC+08:00) Perth
[8 empty] | Custom Equipment | [10 empty] | (UTC+08:00) Taipei
[8 empty] | Custom Branch | [10 empty] | (UTC+08:00) Ulaanbaatar
[8 empty] | Custom Shunt | [10 empty] | (UTC+08:45) Eucla
[8 empty] | Custom Switch | [10 empty] | (UTC+09:00) Chita
[8 empty] | Flexible Load | [10 empty] | (UTC+09:00) Osaka, Sapporo, Tokyo
[8 empty] | Limit Set | [10 empty] | (UTC+09:00) Pyongyang
[8 empty] | Alarm/Event Catalog | [10 empty] | (UTC+09:00) Seoul
[8 empty] | Signal Value Alarm | [10 empty] | (UTC+09:00) Yakutsk
[8 empty] | Analog Alarm Limits | [10 empty] | (UTC+09:30) Adelaide
[8 empty] | Advanced Alarm Limits | [10 empty] | (UTC+09:30) Darwin
[8 empty] | Energy Storage | [10 empty] | (UTC+10:00) Brisbane
[8 empty] | Meter Measurements | [10 empty] | (UTC+10:00) Canberra, Melbourne, Sydney
[8 empty] | Phase Tap Changer | [10 empty] | (UTC+10:00) Guam, Port Moresby
[8 empty] | Static Var Compensator | [10 empty] | (UTC+10:00) Hobart
[8 empty] | Counter IEC | [10 empty] | (UTC+10:00) Vladivostok
[8 empty] | Analog Input IEC | [10 empty] | (UTC+10:30) Lord Howe Island
[8 empty] | Discrete Input IEC | [10 empty] | (UTC+11:00) Bougainville Island
[8 empty] | Analog Output IEC | [10 empty] | (UTC+11:00) Chokurdakh
[8 empty] | Discrete Output IEC | [10 empty] | (UTC+11:00) Magadan
[8 empty] | Sub-Remote Unit IEC104 | [10 empty] | (UTC+11:00) Norfolk Island
[8 empty] | Main Remote Unit IEC104 | [10 empty] | (UTC+11:00) Sakhalin
[8 empty] | Communication Link IEC104 | [10 empty] | (UTC+11:00) Solomon Is., New Caledonia
[8 empty] | Communication Channel IEC104 | [10 empty] | (UTC+12:00) Anadyr, Petropavlovsk-Kamchatsky
[8 empty] | Analog Input DNP3 | [10 empty] | (UTC+12:00) Auckland, Wellington
[8 empty] | Discrete Input DNP3 | [10 empty] | (UTC+12:00) Coordinated Universal Time+12
[8 empty] | Analog Output DNP3 | [10 empty] | (UTC+12:00) Fiji
[8 empty] | Discrete Output DNP3 | [10 empty] | (UTC+12:00) Petropavlovsk-Kamchatsky - Old
[8 empty] | Remote Unit DNP3 | [10 empty] | (UTC+12:45) Chatham Islands
[8 empty] | Communication Link DNP3 | [10 empty] | (UTC+13:00) Coordinated Universal Time+13
[8 empty] | Communication Channel DNP3 | [10 empty] | (UTC+13:00) Nuku'alofa
[8 empty] | Counter DNP3 | [10 empty] | (UTC+13:00) Samoa
[8 empty] | Remote Input DNP3 | [10 empty] | (UTC+14:00) Kiritimati Island
Remote Output DNP3
ICCP Dataset/Transfer Set
ICCP Remote Control Center
ICCP Application Reference
ICCP Association
Analog Processing
DER Group
Terminal Server
Remote Unit IEC101
Communication Link IEC101
Communication Channel IEC101
Serial Link
TCP/IP Link
Calculation Constant Argument
Calculation Signal Argument
Calculation Parameter
Calculation Parameter
Calculation Code
ADMS Analog Point
ADMS Discrete Point
Modbus Analog Input
Modbus Discrete Input
Modbus Analog Output
Modbus Discrete Output
Modbus Remote Unit
Modbus Communication Link
Modbus Communication Channel
Modem
Modem Bank
Modem Link
DNP3 Scan Group
ICCP Network Configuration
2179 Analog Input
2179 Discrete Input
2179 Rate Point
2179 Analog Output
2179 Discrete Output
2179 Remote Unit
2179 Communication Link
2179 Communication Channel
2179 Scan Group
2179 Sub-Remote Unit
Custom1 Analog Input
Custom1 Discrete Input
Custom1 Analog Output
Custom1 Discrete Output
Custom1 Communication Channel
Custom1 Remote Unit
Custom1 Communication Link
Custom2 Analog Input
Custom2 Discrete Input
Custom2 Analog Output
Custom2 Discrete Output
Custom2 Communication Channel
Custom2 Remote Unit
Custom2 Communication Link
Custom3 Analog Input
Custom3 Discrete Input
Custom3 Analog Output
Custom3 Discrete Output
Custom3 Communication Channel
Custom3 Remote Unit
Custom3 Communication Link
61850 Analog Input
61850 Discrete Input
61850 Analog Output
61850 Discrete Output
61850 Communication Channel
61850 Remote Unit
61850 Communication Link
DNP3 Slave Analog Input
DNP3 Slave Discrete Input
DNP3 Slave Analog Output
DNP3 Slave Discrete Output
DNP3 Slave Communication Channel
DNP3 Slave Remote Unit
DNP3 Slave Communication Link
DNP3 Slave Counter
Series5 Analog Input
Series5 Discrete Input
Series5 Analog Output
Series5 Discrete Output
Series5 Remote Unit
Series5 Communication Link
Series5 Communication Channel
Series5 Scan Group
Relay Conditional Scheme
DOM Catalog
Template
Meter Analog Input
Meter Discrete Input
VanComm Remote Unit
VanComm Communication Link
VanComm Communication Channel
Vancomm Scan Group
VanComm Analog Input
VanComm Analog Output
VanComm Discrete Input
VanComm Discrete Output
MD3 Remote Unit
MD3 Communication Link
MD3 Communication Channel
MD3 Scan Group
MD3 Analog Input
MD3 Analog Output
MD3 Discrete Input
MD3 Discrete Output
Conitel Remote Unit
Conitel Communication Link
Conitel Communication Channel
Conitel Scan Group
Conitel Analog Input
Conitel Analog Output
Conitel Discrete Input
Conitel Discrete Output
DNP3 Secure
Template Instance
Temporary Mobile Object
Temporary Cut
Temporary Generator
Temporary Grounding
Temporary Jumper
Temporary Switch
Fault
Temporary Load
Oscillation Processing
Schedule Catalog
IEEE 2030.5 Meter Reading Input
IEEE 2030.5 DER Availability Input
IEEE 2030.5 DER Status Input
IEEE 2030.5 DER Settings Input
IEEE 2030.5 DER Control
IEEE 2030.5 Curve Point
IEEE 2030.5 Group
IEEE 2030.5 End Device
IEEE 2030.5 Communication Link
IEEE 2030.5 Communication Channel
IEC61850 Analog Input
IEC61850 Discrete Input
IEC61850 Analog Output
IEC61850 Discrete Output
IEC61850 Association
IEC61850 Access Point
IEC61850 IED
IEC61850 Report Control Block
IEC Slave Analog Input Server
IEC Slave Discrete Input Server
IEC Slave Counter Input Server
IEC Slave Analog Server
IEC Slave Discrete Output Server
IEC101 Slave Remote Unit
IEC101 Slave Communication Channel
IEC101 Slave Communication Link
IEC61850 SCL File
TLS
IEC Scan Group
IEC61850 Counter
IEEE 2030.5 Group
IEEE 2030.5 DER Aggregator
Advanced Alarm Limits Catalog
Virtual Generator
Generation Control Area
DNP3 Sub-Remote Group
UDPLink
IEC104 Slave Remote Unit
IEC104 Slave Communication Channel
IEC104 Slave Communication Link
Custom1 Counter
Custom2 Counter
Custom3 Counter
MQTT Analog Input
MQTT Discrete Input
MQTT Analog Output
MQTT Discrete Output
Host Client MQTT
Device MQTT
Edge Client MQTT
MQTT Communication Link
MQTT Communication Channel
MQTT Topic
MQTT Remote Point Topic
CommLink Alarm Set
RTU Alarm Set

## ANALÓGICAS (hidden)
Signal Name (TAG) | Signal Alias (Descritivo) | Device Mapping (Equipamento) | Signal Type | Measurement Type | Display Unit | Phases | Alarm Limits | Remote Point Alias | Remote Point Type | Scaling Factor | Input Coordinate (Endereço da Analógica)
045DJGUL00019_MVAR | POT REATIVA | BRK_045DJGUL00019 | Measured Value | Reactive Power | MVAr | ABC |  | DGULRM01DISJMVAR | Analog | 1000 | 1188
045DJGUL00019_0VBC | TENSAO BR | BRK_045DJGUL00019 | Custom | Voltage | kV | B | AlarmLimitVoltage_LL-83,6-Baixo-I-180_L-84,5-Baixo-D-180_H-91,5-Baixo-D-180_HH-92,4-Baixo-I-180 | DGULRM01DISJ0VBC | Analog | 1 | 1002
045DJGUL00019_00MW | POT ATIVA | BRK_045DJGUL00019 | Measured Value | Active Power | MW | ABC |  | DGULRM01DISJ00MW | Analog | 1000 | 1187
045DJGUL00019_00IV | CORRENTE VM | BRK_045DJGUL00019 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-1378,125-Alto-I-1 | DGULRM01DISJ00IV | Analog | 1 | 1006
045DJGUL00019_00IB | CORRENTE BR | BRK_045DJGUL00019 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-1378,125-Alto-I-1 | DGULRM01DISJ00IB | Analog | 1 | 1005
045DJGUL00019_00IN | CORRENTE NE | BRK_045DJGUL00019 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-1378,125-Alto-I-1 | DGULRM01DISJ00IN | Analog | 1 | 1007
045DJGUL00019_00IA | CORRENTE AZ | BRK_045DJGUL00019 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-1378,125-Alto-I-1 | DGULRM01DISJ00IA | Analog | 1 | 1004
045DJGUL00019_00FP | FATOR DE POTENCIA | BRK_045DJGUL00019 | Measured Value | Power Factor | Default | ABC |  | DGULRM01DISJ00FP | Analog | 1 | 1189
045DJGUL00029_00FP | FATOR DE POTENCIA | BRK_045DJGUL00029 | Measured Value | Power Factor | Default | ABC |  | DGULRM02DISJ00FP | Analog | 1 | 1192
045DJGUL00029_00IN | CORRENTE NE | BRK_045DJGUL00029 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-1378,125-Alto-I-1 | DGULRM02DISJ00IN | Analog | 1 | 1014
045DJGUL00029_00IA | CORRENTE AZ | BRK_045DJGUL00029 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-1378,125-Alto-I-1 | DGULRM02DISJ00IA | Analog | 1 | 1011
045DJGUL00029_MVAR | POT REATIVA | BRK_045DJGUL00029 | Measured Value | Reactive Power | MVAr | ABC |  | DGULRM02DISJMVAR | Analog | 1000 | 1191
045DJGUL00029_0VBC | TENSAO BR | BRK_045DJGUL00029 | Custom | Voltage | kV | B | AlarmLimitVoltage_LL-83,6-Baixo-I-180_L-84,5-Baixo-D-180_H-91,5-Baixo-D-180_HH-92,4-Baixo-I-180 | DGULRM02DISJ0VBC | Analog | 1 | 1009
045DJGUL00029_00IB | CORRENTE BR | BRK_045DJGUL00029 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-1378,125-Alto-I-1 | DGULRM02DISJ00IB | Analog | 1 | 1012
045DJGUL00029_00IV | CORRENTE VM | BRK_045DJGUL00029 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-1378,125-Alto-I-1 | DGULRM02DISJ00IV | Analog | 1 | 1013
045DJGUL00029_00MW | POT ATIVA | BRK_045DJGUL00029 | Measured Value | Active Power | MW | ABC |  | DGULRM02DISJ00MW | Analog | 1000 | 1190
045DJGUL00039_MVAR | POT REATIVA | BRK_045DJGUL00039 | Measured Value | Reactive Power | MVAr | ABC |  | DGULSC11DISJMVAR | Analog | 1000 | 1034
045DJGUL00039_0MVA | POT APARENTE | BRK_045DJGUL00039 | Measured Value | Apparent Power | MVA | ABC | AlarmLimitApparent Power_H-33,3-Baixo-D-60 | DGULSC11DISJ0MVA | Analog | 1000 | 1033
045DJGUL00039_0FRQ | FREQUENCIA | BRK_045DJGUL00039 | Measured Value | Frequency | Hz | ABC | AlarmLimitFrequency_L-59,5-Baixo-I-1_H-60,5-Baixo-I-1 | DGULSC11DISJ0FRQ | Analog | 1 | 1031
045DJGUL00039_00MW | POT ATIVA | BRK_045DJGUL00039 | Measured Value | Active Power | MW | ABC |  | DGULSC11DISJ00MW | Analog | 1000 | 1035
045DJGUL00039_00VB | TENSAO BR | BRK_045DJGUL00039 | Measured Value | Voltage | kV | B | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC11DISJ00VB | Analog | 1 | 1037
045DJGUL00039_00IV | CORRENTE VM | BRK_045DJGUL00039 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC11DISJ00IV | Analog | 1 | 1029
045DJGUL00039_00IB | CORRENTE BR | BRK_045DJGUL00039 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC11DISJ00IB | Analog | 1 | 1028
045DJGUL00039_00IN | CORRENTE NE | BRK_045DJGUL00039 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC11DISJ00IN | Analog | 1 | 1030
045DJGUL00039_00IA | CORRENTE AZ | BRK_045DJGUL00039 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2152,5-Baixo-I-0 | DGULSC11DISJ00IA | Analog | 1 | 1027
045DJGUL00039_00FP | FATOR DE POTENCIA | BRK_045DJGUL00039 | Measured Value | Power Factor | Default | ABC |  | DGULSC11DISJ00FP | Analog | 1 | 1032
045DJGUL00039_00VA | TENSAO AZ | BRK_045DJGUL00039 | Measured Value | Voltage | kV | A | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC11DISJ00VA | Analog | 1 | 1036
045DJGUL00039_00VV | TENSAO VM | BRK_045DJGUL00039 | Measured Value | Voltage | kV | C | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC11DISJ00VV | Analog | 1 | 1038
045DJGUL00049_MVAR | POT REATIVA | BRK_045DJGUL00049 | Measured Value | Reactive Power | MVAr | ABC |  | DGULSC12DISJMVAR | Analog | 1000 | 1046
045DJGUL00049_0FRQ | FREQUENCIA | BRK_045DJGUL00049 | Measured Value | Frequency | Hz | ABC | AlarmLimitFrequency_L-59,5-Baixo-I-1_H-60,5-Baixo-I-1 | DGULSC12DISJ0FRQ | Analog | 1 | 1043
045DJGUL00049_00VV | TENSAO VM | BRK_045DJGUL00049 | Measured Value | Voltage | kV | C | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC12DISJ00VV | Analog | 1 | 1050
045DJGUL00049_0MVA | POT APARENTE | BRK_045DJGUL00049 | Measured Value | Apparent Power | MVA | ABC | AlarmLimitApparent Power_H-33,3-Baixo-D-60 | DGULSC12DISJ0MVA | Analog | 1000 | 1045
045DJGUL00049_00VA | TENSAO AZ | BRK_045DJGUL00049 | Measured Value | Voltage | kV | A | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC12DISJ00VA | Analog | 1 | 1048
045DJGUL00049_00VB | TENSAO BR | BRK_045DJGUL00049 | Measured Value | Voltage | kV | B | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC12DISJ00VB | Analog | 1 | 1049
045DJGUL00049_00MW | POT ATIVA | BRK_045DJGUL00049 | Measured Value | Active Power | MW | ABC |  | DGULSC12DISJ00MW | Analog | 1000 | 1047
045DJGUL00049_00IV | CORRENTE VM | BRK_045DJGUL00049 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC12DISJ00IV | Analog | 1 | 1041
045DJGUL00049_00IB | CORRENTE BR | BRK_045DJGUL00049 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC12DISJ00IB | Analog | 1 | 1040
045DJGUL00049_00IN | CORRENTE NE | BRK_045DJGUL00049 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC12DISJ00IN | Analog | 1 | 1042
045DJGUL00049_00IA | CORRENTE AZ | BRK_045DJGUL00049 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC12DISJ00IA | Analog | 1 | 1039
045DJGUL00049_00FP | FATOR DE POTENCIA | BRK_045DJGUL00049 | Measured Value | Power Factor | Default | ABC |  | DGULSC12DISJ00FP | Analog | 1 | 1044
045DJGUL00059_00IB | CORRENTE BR | BRK_045DJGUL00059 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC13DISJ00IB | Analog | 1 | 1052
045DJGUL00059_00FP | FATOR DE POTENCIA | BRK_045DJGUL00059 | Measured Value | Power Factor | Default | ABC |  | DGULSC13DISJ00FP | Analog | 1 | 1056
045DJGUL00059_00IA | CORRENTE AZ | BRK_045DJGUL00059 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC13DISJ00IA | Analog | 1 | 1051
045DJGUL00059_MVAR | POT REATIVA | BRK_045DJGUL00059 | Measured Value | Reactive Power | MVAr | ABC |  | DGULSC13DISJMVAR | Analog | 1000 | 1058
045DJGUL00059_0FRQ | FREQUENCIA | BRK_045DJGUL00059 | Measured Value | Frequency | Hz | ABC | AlarmLimitFrequency_L-59,5-Baixo-I-1_H-60,5-Baixo-I-1 | DGULSC13DISJ0FRQ | Analog | 1 | 1055
045DJGUL00059_00VB | TENSAO BR | BRK_045DJGUL00059 | Measured Value | Voltage | kV | B | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC13DISJ00VB | Analog | 1 | 1061
045DJGUL00059_00VA | TENSAO AZ | BRK_045DJGUL00059 | Measured Value | Voltage | kV | A | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC13DISJ00VA | Analog | 1 | 1060
045DJGUL00059_00VV | TENSAO VM | BRK_045DJGUL00059 | Measured Value | Voltage | kV | C | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC13DISJ00VV | Analog | 1 | 1062
045DJGUL00059_0MVA | POT APARENTE | BRK_045DJGUL00059 | Measured Value | Apparent Power | MVA | ABC | AlarmLimitApparent Power_H-33,3-Baixo-D-60 | DGULSC13DISJ0MVA | Analog | 1000 | 1057
045DJGUL00059_00IV | CORRENTE VM | BRK_045DJGUL00059 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC13DISJ00IV | Analog | 1 | 1053
045DJGUL00059_00MW | POT ATIVA | BRK_045DJGUL00059 | Measured Value | Active Power | MW | ABC |  | DGULSC13DISJ00MW | Analog | 1000 | 1059
045DJGUL00059_00IN | CORRENTE NE | BRK_045DJGUL00059 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC13DISJ00IN | Analog | 1 | 1054
045DJGUL00069_00IV | CORRENTE VM | BRK_045DJGUL00069 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC14DISJ00IV | Analog | 1 | 1065
045DJGUL00069_00MW | POT ATIVA | BRK_045DJGUL00069 | Measured Value | Active Power | MW | ABC |  | DGULSC14DISJ00MW | Analog | 1000 | 1071
045DJGUL00069_00VA | TENSAO AZ | BRK_045DJGUL00069 | Measured Value | Voltage | kV | A | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC14DISJ00VA | Analog | 1 | 1072
045DJGUL00069_00IN | CORRENTE NE | BRK_045DJGUL00069 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC14DISJ00IN | Analog | 1 | 1066
045DJGUL00069_00IB | CORRENTE BR | BRK_045DJGUL00069 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2152,5-Alto-I-1 | DGULSC14DISJ00IB | Analog | 1 | 1064
045DJGUL00069_00FP | FATOR DE POTENCIA | BRK_045DJGUL00069 | Measured Value | Power Factor | Default | ABC |  | DGULSC14DISJ00FP | Analog | 1 | 1068
045DJGUL00069_00IA | CORRENTE AZ | BRK_045DJGUL00069 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2100-Alto-I-1 | DGULSC14DISJ00IA | Analog | 1 | 1063
045DJGUL00069_MVAR | POT REATIVA | BRK_045DJGUL00069 | Measured Value | Reactive Power | MVAr | ABC |  | DGULSC14DISJMVAR | Analog | 1000 | 1070
045DJGUL00069_0MVA | POT APARENTE | BRK_045DJGUL00069 | Measured Value | Apparent Power | MVA | ABC | AlarmLimitApparent Power_H-33,3-Baixo-D-60 | DGULSC14DISJ0MVA | Analog | 1000 | 1069
045DJGUL00069_0FRQ | FREQUENCIA | BRK_045DJGUL00069 | Measured Value | Frequency | Hz | ABC | AlarmLimitFrequency_L-59,5-Baixo-I-1_H-60,5-Baixo-I-1 | DGULSC14DISJ0FRQ | Analog | 1 | 1067
045DJGUL00069_00VB | TENSAO BR | BRK_045DJGUL00069 | Measured Value | Voltage | kV | B | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC14DISJ00VB | Analog | 1 | 1073
045DJGUL00069_00VV | TENSAO VM | BRK_045DJGUL00069 | Measured Value | Voltage | kV | C | AlarmLimitVoltage_LL-13,1-Baixo-I-180_L-13,3-Baixo-D-180_H-14,3-Baixo-D-180_HH-14,5-Baixo-I-180 | DGULSC14DISJ00VV | Analog | 1 | 1074
045DJGUL00109_00IV | CORRENTE VM | BRK_045DJGUL00109 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT10DISJ00IV | Analog | 1 | 1077
045DJGUL00109_00IB | CORRENTE BR | BRK_045DJGUL00109 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT10DISJ00IB | Analog | 1 | 1076
045DJGUL00109_00IA | CORRENTE AZ | BRK_045DJGUL00109 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT10DISJ00IA | Analog | 1 | 1075
045DJGUL00109_00IN | CORRENTE NE | BRK_045DJGUL00109 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT10DISJ00IN | Analog | 1 | 1078
045DJGUL00119_MVAR | POT REATIVA | BRK_045DJGUL00119 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ11DISJMVAR | Analog | 1000 | 1194
045DJGUL00119_00MW | POT ATIVA | BRK_045DJGUL00119 | Measured Value | Active Power | MW | ABC |  | DGULDJ11DISJ00MW | Analog | 1000 | 1193
045DJGUL00119_00IV | CORRENTE VM | BRK_045DJGUL00119 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ11DISJ00IV | Analog | 1 | 1101
045DJGUL00119_00IN | CORRENTE NE | BRK_045DJGUL00119 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ11DISJ00IN | Analog | 1 | 1102
045DJGUL00119_00FP | FATOR DE POTENCIA | BRK_045DJGUL00119 | Measured Value | Power Factor | Default | ABC |  | DGULDJ11DISJ00FP | Analog | 1 | 1195
045DJGUL00119_00IB | CORRENTE BR | BRK_045DJGUL00119 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ11DISJ00IB | Analog | 1 | 1100
045DJGUL00119_00IA | CORRENTE AZ | BRK_045DJGUL00119 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ11DISJ00IA | Analog | 1 | 1099
045DJGUL00129_00MW | POT ATIVA | BRK_045DJGUL00129 | Measured Value | Active Power | MW | ABC |  | DGULDJ12DISJ00MW | Analog | 1000 | 1196
045DJGUL00129_MVAR | POT REATIVA | BRK_045DJGUL00129 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ12DISJMVAR | Analog | 1000 | 1197
045DJGUL00129_00IV | CORRENTE VM | BRK_045DJGUL00129 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ12DISJ00IV | Analog | 1 | 1105
045DJGUL00129_00IN | CORRENTE NE | BRK_045DJGUL00129 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ12DISJ00IN | Analog | 1 | 1106
045DJGUL00129_00IB | CORRENTE BR | BRK_045DJGUL00129 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ12DISJ00IB | Analog | 1 | 1104
045DJGUL00129_00IA | CORRENTE AZ | BRK_045DJGUL00129 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ12DISJ00IA | Analog | 1 | 1103
045DJGUL00129_00FP | FATOR DE POTENCIA | BRK_045DJGUL00129 | Measured Value | Power Factor | Default | ABC |  | DGULDJ12DISJ00FP | Analog | 1 | 1198
045DJGUL00139_MVAR | POT REATIVA | BRK_045DJGUL00139 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ13DISJMVAR | Analog | 1000 | 1200
045DJGUL00139_00MW | POT ATIVA | BRK_045DJGUL00139 | Measured Value | Active Power | MW | ABC |  | DGULDJ13DISJ00MW | Analog | 1000 | 1199
045DJGUL00139_00IV | CORRENTE VM | BRK_045DJGUL00139 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ13DISJ00IV | Analog | 1 | 1109
045DJGUL00139_00IN | CORRENTE NE | BRK_045DJGUL00139 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ13DISJ00IN | Analog | 1 | 1110
045DJGUL00139_00IA | CORRENTE AZ | BRK_045DJGUL00139 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ13DISJ00IA | Analog | 1 | 1107
045DJGUL00139_00FP | FATOR DE POTENCIA | BRK_045DJGUL00139 | Measured Value | Power Factor | Default | ABC |  | DGULDJ13DISJ00FP | Analog | 1 | 1201
045DJGUL00139_00IB | CORRENTE BR | BRK_045DJGUL00139 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ13DISJ00IB | Analog | 1 | 1108
045DJGUL00149_00MW | POT ATIVA | BRK_045DJGUL00149 | Measured Value | Active Power | MW | ABC |  | DGULDJ14DISJ00MW | Analog | 1000 | 1202
045DJGUL00149_00IV | CORRENTE VM | BRK_045DJGUL00149 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ14DISJ00IV | Analog | 1 | 1113
045DJGUL00149_MVAR | POT REATIVA | BRK_045DJGUL00149 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ14DISJMVAR | Analog | 1000 | 1203
045DJGUL00149_00IB | CORRENTE BR | BRK_045DJGUL00149 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ14DISJ00IB | Analog | 1 | 1112
045DJGUL00149_00IN | CORRENTE NE | BRK_045DJGUL00149 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ14DISJ00IN | Analog | 1 | 1114
045DJGUL00149_00IA | CORRENTE AZ | BRK_045DJGUL00149 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ14DISJ00IA | Analog | 1 | 1111
045DJGUL00149_00FP | FATOR DE POTENCIA | BRK_045DJGUL00149 | Measured Value | Power Factor | Default | ABC |  | DGULDJ14DISJ00FP | Analog | 1 | 1204
045DJGUL00159_MVAR | POT REATIVA | BRK_045DJGUL00159 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ15DISJMVAR | Analog | 1000 | 1206
045DJGUL00159_00MW | POT ATIVA | BRK_045DJGUL00159 | Measured Value | Active Power | MW | ABC |  | DGULDJ15DISJ00MW | Analog | 1000 | 1205
045DJGUL00159_00IV | CORRENTE VM | BRK_045DJGUL00159 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ15DISJ00IV | Analog | 1 | 1117
045DJGUL00159_00IN | CORRENTE NE | BRK_045DJGUL00159 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ15DISJ00IN | Analog | 1 | 1118
045DJGUL00159_00IA | CORRENTE AZ | BRK_045DJGUL00159 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ15DISJ00IA | Analog | 1 | 1115
045DJGUL00159_00IB | CORRENTE BR | BRK_045DJGUL00159 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ15DISJ00IB | Analog | 1 | 1116
045DJGUL00159_00FP | FATOR DE POTENCIA | BRK_045DJGUL00159 | Measured Value | Power Factor | Default | ABC |  | DGULDJ15DISJ00FP | Analog | 1 | 1207
045DJGUL00169_MVAR | POT REATIVA | BRK_045DJGUL00169 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ16DISJMVAR | Analog | 1000 | 1209
045DJGUL00169_00IV | CORRENTE VM | BRK_045DJGUL00169 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ16DISJ00IV | Analog | 1 | 1121
045DJGUL00169_00MW | POT ATIVA | BRK_045DJGUL00169 | Measured Value | Active Power | MW | ABC |  | DGULDJ16DISJ00MW | Analog | 1000 | 1208
045DJGUL00169_00IN | CORRENTE NE | BRK_045DJGUL00169 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ16DISJ00IN | Analog | 1 | 1122
045DJGUL00169_00IA | CORRENTE AZ | BRK_045DJGUL00169 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ16DISJ00IA | Analog | 1 | 1119
045DJGUL00169_00FP | FATOR DE POTENCIA | BRK_045DJGUL00169 | Measured Value | Power Factor | Default | ABC |  | DGULDJ16DISJ00FP | Analog | 1 | 1210
045DJGUL00169_00IB | CORRENTE BR | BRK_045DJGUL00169 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ16DISJ00IB | Analog | 1 | 1120
045DJGUL00209_00IV | CORRENTE VM | BRK_045DJGUL00209 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT20DISJ00IV | Analog | 1 | 1081
045DJGUL00209_00IN | CORRENTE NE | BRK_045DJGUL00209 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT20DISJ00IN | Analog | 1 | 1082
045DJGUL00209_00IB | CORRENTE BR | BRK_045DJGUL00209 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT20DISJ00IB | Analog | 1 | 1080
045DJGUL00209_00IA | CORRENTE AZ | BRK_045DJGUL00209 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT20DISJ00IA | Analog | 1 | 1079
045DJGUL00219_00MW | POT ATIVA | BRK_045DJGUL00219 | Measured Value | Active Power | MW | ABC |  | DGULDJ21DISJ00MW | Analog | 1000 | 1211
045DJGUL00219_MVAR | POT REATIVA | BRK_045DJGUL00219 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ21DISJMVAR | Analog | 1000 | 1212
045DJGUL00219_00IV | CORRENTE VM | BRK_045DJGUL00219 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ21DISJ00IV | Analog | 1 | 1125
045DJGUL00219_00IN | CORRENTE NE | BRK_045DJGUL00219 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ21DISJ00IN | Analog | 1 | 1126
045DJGUL00219_00IB | CORRENTE BR | BRK_045DJGUL00219 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ21DISJ00IB | Analog | 1 | 1124
045DJGUL00219_00IA | CORRENTE AZ | BRK_045DJGUL00219 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ21DISJ00IA | Analog | 1 | 1123
045DJGUL00219_00FP | FATOR DE POTENCIA | BRK_045DJGUL00219 | Measured Value | Power Factor | Default | ABC |  | DGULDJ21DISJ00FP | Analog | 1 | 1213
045DJGUL00229_MVAR | POT REATIVA | BRK_045DJGUL00229 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ22DISJMVAR | Analog | 1000 | 1215
045DJGUL00229_00IV | CORRENTE VM | BRK_045DJGUL00229 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ22DISJ00IV | Analog | 1 | 1129
045DJGUL00229_00IB | CORRENTE BR | BRK_045DJGUL00229 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ22DISJ00IB | Analog | 1 | 1128
045DJGUL00229_00MW | POT ATIVA | BRK_045DJGUL00229 | Measured Value | Active Power | MW | ABC |  | DGULDJ22DISJ00MW | Analog | 1000 | 1214
045DJGUL00229_00IN | CORRENTE NE | BRK_045DJGUL00229 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ22DISJ00IN | Analog | 1 | 1130
045DJGUL00229_00IA | CORRENTE AZ | BRK_045DJGUL00229 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ22DISJ00IA | Analog | 1 | 1127
045DJGUL00229_00FP | FATOR DE POTENCIA | BRK_045DJGUL00229 | Measured Value | Power Factor | Default | ABC |  | DGULDJ22DISJ00FP | Analog | 1 | 1216
045DJGUL00239_00FP | FATOR DE POTENCIA | BRK_045DJGUL00239 | Measured Value | Power Factor | Default | ABC |  | DGULDJ23DISJ00FP | Analog | 1 | 1219
045DJGUL00239_MVAR | POT REATIVA | BRK_045DJGUL00239 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ23DISJMVAR | Analog | 1000 | 1218
045DJGUL00239_00MW | POT ATIVA | BRK_045DJGUL00239 | Measured Value | Active Power | MW | ABC |  | DGULDJ23DISJ00MW | Analog | 1000 | 1217
045DJGUL00239_00IV | CORRENTE VM | BRK_045DJGUL00239 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ23DISJ00IV | Analog | 1 | 1133
045DJGUL00239_00IB | CORRENTE BR | BRK_045DJGUL00239 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ23DISJ00IB | Analog | 1 | 1132
045DJGUL00239_00IN | CORRENTE NE | BRK_045DJGUL00239 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ23DISJ00IN | Analog | 1 | 1134
045DJGUL00239_00IA | CORRENTE AZ | BRK_045DJGUL00239 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ23DISJ00IA | Analog | 1 | 1131
045DJGUL00249_MVAR | POT REATIVA | BRK_045DJGUL00249 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ24DISJMVAR | Analog | 1000 | 1221
045DJGUL00249_00MW | POT ATIVA | BRK_045DJGUL00249 | Measured Value | Active Power | MW | ABC |  | DGULDJ24DISJ00MW | Analog | 1000 | 1220
045DJGUL00249_00IV | CORRENTE VM | BRK_045DJGUL00249 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ24DISJ00IV | Analog | 1 | 1137
045DJGUL00249_00IN | CORRENTE NE | BRK_045DJGUL00249 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ24DISJ00IN | Analog | 1 | 1138
045DJGUL00249_00IB | CORRENTE BR | BRK_045DJGUL00249 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ24DISJ00IB | Analog | 1 | 1136
045DJGUL00249_00IA | CORRENTE AZ | BRK_045DJGUL00249 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ24DISJ00IA | Analog | 1 | 1135
045DJGUL00249_00FP | FATOR DE POTENCIA | BRK_045DJGUL00249 | Measured Value | Power Factor | Default | ABC |  | DGULDJ24DISJ00FP | Analog | 1 | 1222
045DJGUL00259_MVAR | POT REATIVA | BRK_045DJGUL00259 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ25DISJMVAR | Analog | 1000 | 1224
045DJGUL00259_00MW | POT ATIVA | BRK_045DJGUL00259 | Measured Value | Active Power | MW | ABC |  | DGULDJ25DISJ00MW | Analog | 1000 | 1223
045DJGUL00259_00IN | CORRENTE NE | BRK_045DJGUL00259 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ25DISJ00IN | Analog | 1 | 1142
045DJGUL00259_00IA | CORRENTE AZ | BRK_045DJGUL00259 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ25DISJ00IA | Analog | 1 | 1139
045DJGUL00259_00FP | FATOR DE POTENCIA | BRK_045DJGUL00259 | Measured Value | Power Factor | Default | ABC |  | DGULDJ25DISJ00FP | Analog | 1 | 1225
045DJGUL00259_00IV | CORRENTE VM | BRK_045DJGUL00259 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ25DISJ00IV | Analog | 1 | 1141
045DJGUL00259_00IB | CORRENTE BR | BRK_045DJGUL00259 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ25DISJ00IB | Analog | 1 | 1140
045DJGUL00269_MVAR | POT REATIVA | BRK_045DJGUL00269 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ26DISJMVAR | Analog | 1000 | 1227
045DJGUL00269_00MW | POT ATIVA | BRK_045DJGUL00269 | Measured Value | Active Power | MW | ABC |  | DGULDJ26DISJ00MW | Analog | 1000 | 1226
045DJGUL00269_00IV | CORRENTE VM | BRK_045DJGUL00269 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ26DISJ00IV | Analog | 1 | 1145
045DJGUL00269_00IN | CORRENTE NE | BRK_045DJGUL00269 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ26DISJ00IN | Analog | 1 | 1146
045DJGUL00269_00IB | CORRENTE BR | BRK_045DJGUL00269 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ26DISJ00IB | Analog | 1 | 1144
045DJGUL00269_00IA | CORRENTE AZ | BRK_045DJGUL00269 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ26DISJ00IA | Analog | 1 | 1143
045DJGUL00269_00FP | FATOR DE POTENCIA | BRK_045DJGUL00269 | Measured Value | Power Factor | Default | ABC |  | DGULDJ26DISJ00FP | Analog | 1 | 1228
045DJGUL00309_00IN | CORRENTE NE | BRK_045DJGUL00309 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT30DISJ00IN | Analog | 1 | 1086
045DJGUL00309_00IV | CORRENTE VM | BRK_045DJGUL00309 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT30DISJ00IV | Analog | 1 | 1085
045DJGUL00309_00IB | CORRENTE BR | BRK_045DJGUL00309 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT30DISJ00IB | Analog | 1 | 1084
045DJGUL00309_00IA | CORRENTE AZ | BRK_045DJGUL00309 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT30DISJ00IA | Analog | 1 | 1083
045DJGUL00319_00IA | CORRENTE AZ | BRK_045DJGUL00319 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ31DISJ00IA | Analog | 1 | 1147
045DJGUL00319_00FP | FATOR DE POTENCIA | BRK_045DJGUL00319 | Measured Value | Power Factor | Default | ABC |  | DGULDJ31DISJ00FP | Analog | 1 | 1231
045DJGUL00319_MVAR | POT REATIVA | BRK_045DJGUL00319 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ31DISJMVAR | Analog | 1000 | 1230
045DJGUL00319_00MW | POT ATIVA | BRK_045DJGUL00319 | Measured Value | Active Power | MW | ABC |  | DGULDJ31DISJ00MW | Analog | 1000 | 1229
045DJGUL00319_00IV | CORRENTE VM | BRK_045DJGUL00319 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ31DISJ00IV | Analog | 1 | 1149
045DJGUL00319_00IB | CORRENTE BR | BRK_045DJGUL00319 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ31DISJ00IB | Analog | 1 | 1148
045DJGUL00319_00IN | CORRENTE NE | BRK_045DJGUL00319 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ31DISJ00IN | Analog | 1 | 1150
045DJGUL00329_MVAR | POT REATIVA | BRK_045DJGUL00329 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ32DISJMVAR | Analog | 1000 | 1233
045DJGUL00329_00MW | POT ATIVA | BRK_045DJGUL00329 | Measured Value | Active Power | MW | ABC |  | DGULDJ32DISJ00MW | Analog | 1000 | 1232
045DJGUL00329_00IV | CORRENTE VM | BRK_045DJGUL00329 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ32DISJ00IV | Analog | 1 | 1153
045DJGUL00329_00IN | CORRENTE NE | BRK_045DJGUL00329 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ32DISJ00IN | Analog | 1 | 1154
045DJGUL00329_00FP | FATOR DE POTENCIA | BRK_045DJGUL00329 | Measured Value | Power Factor | Default | ABC |  | DGULDJ32DISJ00FP | Analog | 1 | 1234
045DJGUL00329_00IB | CORRENTE BR | BRK_045DJGUL00329 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ32DISJ00IB | Analog | 1 | 1152
045DJGUL00329_00IA | CORRENTE AZ | BRK_045DJGUL00329 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ32DISJ00IA | Analog | 1 | 1151
045DJGUL00339_MVAR | POT REATIVA | BRK_045DJGUL00339 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ33DISJMVAR | Analog | 1000 | 1236
045DJGUL00339_00IN | CORRENTE NE | BRK_045DJGUL00339 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ33DISJ00IN | Analog | 1 | 1158
045DJGUL00339_00IB | CORRENTE BR | BRK_045DJGUL00339 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ33DISJ00IB | Analog | 1 | 1156
045DJGUL00339_00IA | CORRENTE AZ | BRK_045DJGUL00339 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ33DISJ00IA | Analog | 1 | 1155
045DJGUL00339_00MW | POT ATIVA | BRK_045DJGUL00339 | Measured Value | Active Power | MW | ABC |  | DGULDJ33DISJ00MW | Analog | 1000 | 1235
045DJGUL00339_00IV | CORRENTE VM | BRK_045DJGUL00339 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ33DISJ00IV | Analog | 1 | 1157
045DJGUL00339_00FP | FATOR DE POTENCIA | BRK_045DJGUL00339 | Measured Value | Power Factor | Default | ABC |  | DGULDJ33DISJ00FP | Analog | 1 | 1237
045DJGUL00349_00IV | CORRENTE VM | BRK_045DJGUL00349 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ34DISJ00IV | Analog | 1 | 1161
045DJGUL00349_MVAR | POT REATIVA | BRK_045DJGUL00349 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ34DISJMVAR | Analog | 1000 | 1239
045DJGUL00349_00IN | CORRENTE NE | BRK_045DJGUL00349 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ34DISJ00IN | Analog | 1 | 1162
045DJGUL00349_00IB | CORRENTE BR | BRK_045DJGUL00349 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ34DISJ00IB | Analog | 1 | 1160
045DJGUL00349_00IA | CORRENTE AZ | BRK_045DJGUL00349 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ34DISJ00IA | Analog | 1 | 1159
045DJGUL00349_00MW | POT ATIVA | BRK_045DJGUL00349 | Measured Value | Active Power | MW | ABC |  | DGULDJ34DISJ00MW | Analog | 1000 | 1238
045DJGUL00349_00FP | FATOR DE POTENCIA | BRK_045DJGUL00349 | Measured Value | Power Factor | Default | ABC |  | DGULDJ34DISJ00FP | Analog | 1 | 1240
045DJGUL00359_MVAR | POT REATIVA | BRK_045DJGUL00359 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ35DISJMVAR | Analog | 1000 | 1242
045DJGUL00359_00MW | POT ATIVA | BRK_045DJGUL00359 | Measured Value | Active Power | MW | ABC |  | DGULDJ35DISJ00MW | Analog | 1000 | 1241
045DJGUL00359_00IV | CORRENTE VM | BRK_045DJGUL00359 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ35DISJ00IV | Analog | 1 | 1165
045DJGUL00359_00IN | CORRENTE NE | BRK_045DJGUL00359 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ35DISJ00IN | Analog | 1 | 1166
045DJGUL00359_00IB | CORRENTE BR | BRK_045DJGUL00359 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ35DISJ00IB | Analog | 1 | 1164
045DJGUL00359_00IA | CORRENTE AZ | BRK_045DJGUL00359 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ35DISJ00IA | Analog | 1 | 1163
045DJGUL00359_00FP | FATOR DE POTENCIA | BRK_045DJGUL00359 | Measured Value | Power Factor | Default | ABC |  | DGULDJ35DISJ00FP | Analog | 1 | 1243
045DJGUL00369_MVAR | POT REATIVA | BRK_045DJGUL00369 | Measured Value | Reactive Power | MVAr | ABC |  | DGULDJ36DISJMVAR | Analog | 1000 | 1245
045DJGUL00369_00MW | POT ATIVA | BRK_045DJGUL00369 | Measured Value | Active Power | MW | ABC |  | DGULDJ36DISJ00MW | Analog | 1000 | 1244
045DJGUL00369_00IN | CORRENTE NE | BRK_045DJGUL00369 | Measured Value | Current | A | N | AlarmLimitCurrent_H-100-Baixo-D-60 | DGULDJ36DISJ00IN | Analog | 1 | 1170
045DJGUL00369_00IV | CORRENTE VM | BRK_045DJGUL00369 | Measured Value | Current | A | C | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ36DISJ00IV | Analog | 1 | 1169
045DJGUL00369_00IB | CORRENTE BR | BRK_045DJGUL00369 | Measured Value | Current | A | B | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ36DISJ00IB | Analog | 1 | 1168
045DJGUL00369_00IA | CORRENTE AZ | BRK_045DJGUL00369 | Measured Value | Current | A | A | AlarmLimitCurrent_H-420-Baixo-D-60 | DGULDJ36DISJ00IA | Analog | 1 | 1167
045DJGUL00369_00FP | FATOR DE POTENCIA | BRK_045DJGUL00369 | Measured Value | Power Factor | Default | ABC |  | DGULDJ36DISJ00FP | Analog | 1 | 1246
045DJGUL00409_00IV | CORRENTE VM | BRK_045DJGUL00409 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT40DISJ00IV | Analog | 1 | 1089
045DJGUL00409_00IA | CORRENTE AZ | BRK_045DJGUL00409 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT40DISJ00IA | Analog | 1 | 1087
045DJGUL00409_00IN | CORRENTE NE | BRK_045DJGUL00409 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT40DISJ00IN | Analog | 1 | 1090
045DJGUL00409_00IB | CORRENTE BR | BRK_045DJGUL00409 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT40DISJ00IB | Analog | 1 | 1088
045DJGUL00509_00IB | CORRENTE BR | BRK_045DJGUL00509 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT50DISJ00IB | Analog | 1 | 1092
045DJGUL00509_00IA | CORRENTE AZ | BRK_045DJGUL00509 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT50DISJ00IA | Analog | 1 | 1091
045DJGUL00509_00IV | CORRENTE VM | BRK_045DJGUL00509 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT50DISJ00IV | Analog | 1 | 1093
045DJGUL00509_00IN | CORRENTE NE | BRK_045DJGUL00509 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT50DISJ00IN | Analog | 1 | 1094
045DJGUL00609_00IV | CORRENTE VM | BRK_045DJGUL00609 | Measured Value | Current | A | C | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT60DISJ00IV | Analog | 1 | 1097
045DJGUL00609_00IN | CORRENTE NE | BRK_045DJGUL00609 | Measured Value | Current | A | N | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT60DISJ00IN | Analog | 1 | 1098
045DJGUL00609_00IB | CORRENTE BR | BRK_045DJGUL00609 | Measured Value | Current | A | B | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT60DISJ00IB | Analog | 1 | 1096
045DJGUL00609_00IA | CORRENTE AZ | BRK_045DJGUL00609 | Measured Value | Current | A | A | AlarmLimitCurrent_HH-2205-Alto-I-1 | DGULIT60DISJ00IA | Analog | 1 | 1095
045DJGULSGERL_0VCC | TENSAO VCC | GERAL_GUL | Custom | Voltage | V | Unknown | AlarmLimitVoltage_LL-48-Alto-I-1_HH-56-Alto-I-1 | DGUL0SAGRETF0VCC | Analog | 0.001 | 1171
045SAGUL00019_00VV | TENSAO VM | SA_045SAGUL00019_8552368 | Measured Value | Voltage | V | C |  | DGULSAX1RETF00VV | Analog | 0.001 | 1174
045SAGUL00019_00VB | TENSAO BR | SA_045SAGUL00019_8552368 | Measured Value | Voltage | V | B |  | DGULSAX1RETF00VB | Analog | 0.001 | 1173
045SAGUL00019_00VA | TENSAO AZ | SA_045SAGUL00019_8552368 | Measured Value | Voltage | V | A |  | DGULSAX1RETF00VA | Analog | 0.001 | 1172
045SAGUL00029_00VB | TENSAO BR | SA_045SAGUL00029_8552218 | Measured Value | Voltage | V | B |  | DGULSAX2RETF00VB | Analog | 0.001 | 1176
045SAGUL00029_00VV | TENSAO VM | SA_045SAGUL00029_8552218 | Measured Value | Voltage | V | C |  | DGULSAX2RETF00VV | Analog | 0.001 | 1177
045SAGUL00029_00VA | TENSAO AZ | SA_045SAGUL00029_8552218 | Measured Value | Voltage | V | A |  | DGULSAX2RETF00VA | Analog | 0.001 | 1175
045SAGUL00039_00VB | TENSAO BR | SA_045SAGUL00039_8553013 | Measured Value | Voltage | V | B |  | DGULSAX3RETF00VB | Analog | 0.001 | 1179
045SAGUL00039_00VV | TENSAO VM | SA_045SAGUL00039_8553013 | Measured Value | Voltage | V | C |  | DGULSAX3RETF00VV | Analog | 0.001 | 1180
045SAGUL00039_00VA | TENSAO AZ | SA_045SAGUL00039_8553013 | Measured Value | Voltage | V | A |  | DGULSAX3RETF00VA | Analog | 0.001 | 1178
045TRGUL00019_049A | TEMP ENROL | TS_045TRGUL00019_8553141 | Measured Value | Temperature | C | Unknown | AlarmLimitTemperature_HH-110,25-Alto-I-1 | DGULTR01TRFO049A | Analog | 1 | 1016
045TRGUL00019_0026 | TEMP OLEO | TS_045TRGUL00019_8553141 | Measured Value | Temperature | C | Unknown | AlarmLimitTemperature_HH-93,7125-Alto-I-1 | DGULTR01TRFO0026 | Analog | 1 | 1015
045TRGUL00029_049A | TEMP ENROL | TS_045TRGUL00029_8553116 | Measured Value | Temperature | C | Unknown | AlarmLimitTemperature_HH-110,25-Alto-I-1 | DGULTR02TRFO049A | Analog | 1 | 1019
045TRGUL00029_0026 | TEMP OLEO | TS_045TRGUL00029_8553116 | Measured Value | Temperature | C | Unknown | AlarmLimitTemperature_HH-93,7125-Alto-I-1 | DGULTR02TRFO0026 | Analog | 1 | 1018
045TRGUL00039_049A | TEMP ENROL | TS_045TRGUL00039_8553071 | Measured Value | Temperature | C | Unknown | AlarmLimitTemperature_HH-110,25-Alto-I-1 | DGULTR03TRFO049A | Analog | 1 | 1022
045TRGUL00039_0026 | TEMP OLEO | TS_045TRGUL00039_8553071 | Measured Value | Temperature | C | Unknown | AlarmLimitTemperature_HH-93,7125-Alto-I-1 | DGULTR03TRFO0026 | Analog | 1 | 1021
045TRGUL00049_049A | TEMP ENROL | TS_045TRGUL00049_8553122 | Measured Value | Temperature | C | Unknown | AlarmLimitTemperature_HH-110,25-Alto-I-1 | DGULTR04TRFO049A | Analog | 1 | 1025
045TRGUL00049_0026 | TEMP OLEO | TS_045TRGUL00049_8553122 | Measured Value | Temperature | C | Unknown | AlarmLimitTemperature_HH-93,7125-Alto-I-1 | DGULTR04TRFO0026 | Analog | 1 | 1024

## DIGITAIS-COMANDO
Signal TAG | tag0 | tag1 | tag2 | DIG / CMD | OBS | HLEVEL | Signal Alias (Descritivo) | Descritivo estados | estados SCADA | estado 0 | estado 1 | estado 2 | estado 3 | Remote Point Type | Input Data Type | Input Coord. (Endereço da Digital) | Output Data Type | Output Coord. (Endereço do Comando) | Device Mapping (Equipamento) | Message Mapping
045CSGUL32369_FLTC | 045 | CSGUL32369_ | FLTC | DIGITAL |  | SECC. 3236 | 89 TENSAO CC |  | 0;1;2;3 | NORMAL | FALTA
045CSGUL32369_CBTL | 045 | CSGUL32369_ | CBTL | DIGITAL |  | SECC. 3236 | SECC CH BLOQ TELECOM | SERVIÇO;BLOQUEADO;; | 1;0;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 60 |  |  | DIS_045CSGUL32369 | 52 CH BLOQ TELECOMANDO
045CSGUL32369_0EST | 045 | CSGUL32369_ | 0EST | COMANDO | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3236 | SECCIONADORA - 3236 | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTA | FECHADA | INVALIDA | Discrete | Single-Bit | 59 | Multibit | 2023;2024 | DIS_045CSGUL32369
045CSGUL34479_FLTC | 045 | CSGUL34479_ | FLTC | DIGITAL |  | SECC. 3447 | 89 TENSAO CC |  | 0;1;2;3 | NORMAL | FALTA
045CSGUL34479_CBTL | 045 | CSGUL34479_ | CBTL | DIGITAL |  | SECC. 3447 | SECC CH BLOQ TELECOM | SERVIÇO;BLOQUEADO;; | 1;0;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 58 |  |  | DIS_045CSGUL34479 | 52 CH BLOQ TELECOMANDO
045CSGUL34479_0EST | 045 | CSGUL34479_ | 0EST | COMANDO | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3447 | SECCIONADORA -3447 | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTA | FECHADA | INVALIDA | Discrete | Single-Bit | 57 | Multibit | 2021;2022 | DIS_045CSGUL34479
045CSGUL39939_0EST | 045 | CSGUL39939_ | 0EST | DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3993 | SECCIONADORA - 3993 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 7 |  |  | DIS_045CSGUL39939
045CSGUL39949_0EST | 045 | CSGUL39949_ | 0EST | DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3994 | SECCIONADORA - 3994 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 27 |  |  | DIS_045CSGUL39949
045CSGUL39959_0EST | 045 | CSGUL39959_ | 0EST | DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3995 | SECCIONADORA - 3995 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 43 |  |  | DIS_045CSGUL39959
045CSGUL39969_0EST | 045 | CSGUL39969_ | 0EST | DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3996 | SECCIONADORA - 3996 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 44 |  |  | DIS_045CSGUL39969
045CSGUL39979_0EST | 045 | CSGUL39979_ | 0EST | DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3997 | SECCIONADORA - 3997 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 41 |  |  | DIS_045CSGUL39979
045CSGUL39989_0EST | 045 | CSGUL39989_ | 0EST | DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3998 | SECCIONADORA - 3998 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 42 |  |  | DIS_045CSGUL39989
045CSGUL39999_FLTC | 045 | CSGUL39999_ | FLTC | DIGITAL |  | SECC. 3999 | 89 TENSAO CC |  | 0;1;2;3 | NORMAL | FALTA
045CSGUL39999_CBTL | 045 | CSGUL39999_ | CBTL | DIGITAL |  | SECC. 3999 | SECC CH BLOQ TELECOM | SERVIÇO;BLOQUEADO;; | 1;0;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 46 |  |  | DIS_045CSGUL39999 | 52 CH BLOQ TELECOMANDO
045CSGUL39999_0EST | 045 | CSGUL39999_ | 0EST | COMANDO | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 3999 | SECCIONADORA - 3999 | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTA | FECHADA | INVALIDA | Discrete | Single-Bit | 45 | Multibit | 2009;2010 | DIS_045CSGUL39999
045CSGUL40009_FLTC | 045 | CSGUL40009_ | FLTC | DIGITAL |  | SECC. 4000 | 89 TENSAO CC |  | 0;1;2;3 | NORMAL | FALTA
045CSGUL40009_CBTL | 045 | CSGUL40009_ | CBTL | DIGITAL |  | SECC. 4000 | SECC CH BLOQ TELECOM | SERVIÇO;BLOQUEADO;; | 1;0;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 48 |  |  | DIS_045CSGUL40009 | 52 CH BLOQ TELECOMANDO
045CSGUL40009_0EST | 045 | CSGUL40009_ | 0EST | COMANDO | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 4000 | SECCIONADORA - 4000 | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTA | FECHADA | INVALIDA | Discrete | Single-Bit | 47 | Multibit | 2011;2012 | DIS_045CSGUL40009
045CSGUL40019_FLTC | 045 | CSGUL40019_ | FLTC | DIGITAL |  | SECC. 4001 | 89 TENSAO CC |  | 0;1;2;3 | NORMAL | FALTA
045CSGUL40019_CBTL | 045 | CSGUL40019_ | CBTL | DIGITAL |  | SECC. 4001 | SECC CH BLOQ TELECOM | SERVIÇO;BLOQUEADO;; | 1;0;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 50 |  |  | DIS_045CSGUL40019 | 52 CH BLOQ TELECOMANDO
045CSGUL40019_0EST | 045 | CSGUL40019_ | 0EST | COMANDO | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 4001 | SECCIONADORA - 4001 | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTA | FECHADA | INVALIDA | Discrete | Single-Bit | 49 | Multibit | 2013;2014 | DIS_045CSGUL40019
045CSGUL40029_FLTC | 045 | CSGUL40029_ | FLTC | DIGITAL |  | SECC. 4002 | 89 TENSAO CC |  | 0;1;2;3 | NORMAL | FALTA
045CSGUL40029_CBTL | 045 | CSGUL40029_ | CBTL | DIGITAL |  | SECC. 4002 | SECC CH BLOQ TELECOM | SERVIÇO;BLOQUEADO;; | 1;0;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 52 |  |  | DIS_045CSGUL40029 | 52 CH BLOQ TELECOMANDO
045CSGUL40029_0EST | 045 | CSGUL40029_ | 0EST | COMANDO | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 4002 | SECCIONADORA - 4002 | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTA | FECHADA | INVALIDA | Discrete | Single-Bit | 51 | Multibit | 2015;2016 | DIS_045CSGUL40029
045CSGUL40039_FLTC | 045 | CSGUL40039_ | FLTC | DIGITAL |  | SECC. 4003 | 89 TENSAO CC |  | 0;1;2;3 | NORMAL | FALTA
045CSGUL40039_CBTL | 045 | CSGUL40039_ | CBTL | DIGITAL |  | SECC. 4003 | SECC CH BLOQ TELECOM | SERVIÇO;BLOQUEADO;; | 1;0;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 54 |  |  | DIS_045CSGUL40039 | 52 CH BLOQ TELECOMANDO
045CSGUL40039_0EST | 045 | CSGUL40039_ | 0EST | COMANDO | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 4003 | SECCIONADORA - 4003 | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTA | FECHADA | INVALIDA | Discrete | Single-Bit | 53 | Multibit | 2017;2018 | DIS_045CSGUL40039
045CSGUL40049_FLTC | 045 | CSGUL40049_ | FLTC | DIGITAL |  | SECC. 4004 | 89 TENSAO CC |  | 0;1;2;3 | NORMAL | FALTA
045CSGUL40049_CBTL | 045 | CSGUL40049_ | CBTL | DIGITAL |  | SECC. 4004 | SECC CH BLOQ TELECOM | SERVIÇO;BLOQUEADO;; | 1;0;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 56 |  |  | DIS_045CSGUL40049 | 52 CH BLOQ TELECOMANDO
045CSGUL40049_0EST | 045 | CSGUL40049_ | 0EST | COMANDO | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SECC. 4004 | SECCIONADORA - 4004 | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTA | FECHADA | INVALIDA | Discrete | Single-Bit | 55 | Multibit | 2019;2020 | DIS_045CSGUL40049
045DJGUL00019_027I | 045 | DJGUL00019_ | 027I | DIGITAL |  | DJ01 | 27 PROT SUB TENSÃO | NORMAL;ATUADO;2;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 18 |  |  | BRK_045DJGUL00019_Multifuncional_PE
045DJGUL00019_50FA | 045 | DJGUL00019_ | 50FA | DIGITAL |  | DJ01 | 50 PROT AZ | NORMAL;ATUADO;2;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 2 |  |  | BRK_045DJGUL00019_50_RS
045DJGUL00019_50FB | 045 | DJGUL00019_ | 50FB | DIGITAL |  | DJ01 | 50 PROT BR | NORMAL;ATUADO;2;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 3 |  |  | BRK_045DJGUL00019_50_RS
045DJGUL00019_50NE | 045 | DJGUL00019_ | 50NE | DIGITAL |  | DJ01 | 50 PROT NE | NORMAL;ATUADO;2;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 5 |  |  | BRK_045DJGUL00019_50N_RS
045DJGUL00019_50FV | 045 | DJGUL00019_ | 50FV | DIGITAL |  | DJ01 | 50 PROT VM | NORMAL;ATUADO;2;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 4 |  |  | BRK_045DJGUL00019_50_RS
045DJGUL00019_51FA | 045 | DJGUL00019_ | 51FA | DIGITAL |  | DJ01 | 51 PROT AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00019_51AP | 045 | DJGUL00019_ | 51AP | DIGITAL | N2= ELIPSE | DJ01 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00019_51FB | 045 | DJGUL00019_ | 51FB | DIGITAL |  | DJ01 | 51 PROT BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00019_51BP | 045 | DJGUL00019_ | 51BP | DIGITAL | N2= ELIPSE | DJ01 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00019_51NE | 045 | DJGUL00019_ | 51NE | DIGITAL |  | DJ01 | 51 PROT NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00019_51NP | 045 | DJGUL00019_ | 51NP | DIGITAL | N2= ELIPSE | DJ01 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00019_51FV | 045 | DJGUL00019_ | 51FV | DIGITAL |  | DJ01 | 51 PROT VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00019_51VP | 045 | DJGUL00019_ | 51VP | DIGITAL | N2= ELIPSE | DJ01 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00019_CBTL | 045 | DJGUL00019_ | CBTL | DIGITAL |  | DJ01 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;2;3 | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 14 |  |  | BRK_045DJGUL00019 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00019_0DPT | 045 | DJGUL00019_ | 0DPT | DIGITAL |  | DJ01 | 52 DISJ DESLIG PROTEÇÃO |  | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00019_SF61 | 045 | DJGUL00019_ | SF61 | DIGITAL |  | DJ01 | 52 DISJ SF6 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 998 |  |  | BRK_045DJGUL00019 | 52 DISJ SF6 1º EST
045DJGUL00019_SF62 | 045 | DJGUL00019_ | SF62 | DIGITAL |  | DJ01 | 52 DISJ SF6 2º EST | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 269 |  |  | BRK_045DJGUL00019_Multifuncional_PE | 52 DISJ SF6 2º EST
045DJGUL00019_FLTC | 045 | DJGUL00019_ | FLTC | DIGITAL |  | DJ01 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 9 |  |  | BRK_045DJGUL00019
045DJGUL00019_52ML | 045 | DJGUL00019_ | 52ML | DIGITAL |  | DJ01 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;2;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 20 |  |  | BRK_045DJGUL00019
045DJGUL00019_52BG | 045 | DJGUL00019_ | 52BG | DIGITAL |  | DJ01 | 52 DJ BLOQ GERAL | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 8 |  |  | BRK_045DJGUL00019_Multifuncional_PE
045DJGUL00019_INAT | 045 | DJGUL00019_ | INAT | DIGITAL | N2= ELIPSE | DJ01 | 52 INATIVIDADE |  | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00019_TADJ | 045 | DJGUL00019_ | TADJ | DIGITAL | N2= ELIPSE | DJ01 | 52 TEMPO ABERTURA |  | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00019_00TM | 045 | DJGUL00019_ | 00TM | DIGITAL | N2= ELIPSE | DJ01 | 52 TEMPO CARREGAR MOLA |  | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00019_TFDJ | 045 | DJGUL00019_ | TFDJ | DIGITAL | N2= ELIPSE | DJ01 | 52 TEMPO FECHAMENTO |  | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00019_00FD | 045 | DJGUL00019_ | 00FD | DIGITAL |  | DJ01 | 79 FALHA LIGAR DJ |  | 0;1;2;3 | NORMAL | ALARME
45DJGUL00019_79BA | 045 | DJGUL00019_ | 79BA | DIGITAL |  | DJ01 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO
045DJGUL00019_OO79 | 045 | DJGUL00019_ | OO79 | COMANDO |  | DJ01 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 11 | Multibit | 2004;2003 | BRK_045DJGUL00019 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00019_BAIS | 045 | DJGUL00019_ | BAIS | DIGITAL |  | DJ01 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 10 |  |  | BRK_045DJGUL00019
045DJGUL00019_0EST | 045 | DJGUL00019_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ01 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVALIDO | Discrete | Single-Bit | 6 | Multibit | 2001;2002 | BRK_045DJGUL00019 | 0EST DIGITAL DUPLA
045DJGUL00019_DJTP | 045 | DJGUL00019_ | DJTP | DIGITAL |  | DJ01 | DISJUNTOR TP | ARMADO;DESARMADO;2;3 | 0;1;2;3 | ARMADO | DESARMADO
045DJGUL00019_UCGS | 045 | DJGUL00019_ | UCGS | DIGITAL |  | DJ01 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;2;3 | 0;1;2;3 | NORMAL | FALHA
045DJGUL00019_MREQ | 045 | DJGUL00019_ | MREQ | DIGITAL | N2= ELIPSE | DJ01 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;2;3 | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00019_94CT | 045 | DJGUL00019_ | 94CT | DIGITAL |  | DJ01 | RELE AUX. CORTA - TRIP | NORMAL;DEFEITO;2;3 | 0;1;2;3 | NORMAL | DEFEITO
045DJGUL00019_94T1 | 045 | DJGUL00019_ | 94T1 | DIGITAL | N2= ELIPSE | DJ01 | RELE AUX. CORTA - TRIP TR1 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00019_94T2 | 045 | DJGUL00019_ | 94T2 | DIGITAL | N2= ELIPSE | DJ01 | RELE AUX. CORTA - TRIP TR2 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00019_94T3 | 045 | DJGUL00019_ | 94T3 | DIGITAL | N2= ELIPSE | DJ01 | RELE AUX. CORTA - TRIP TR3 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00019_94T4 | 045 | DJGUL00019_ | 94T4 | DIGITAL | N2= ELIPSE | DJ01 | RELE AUX. CORTA - TRIP TR4 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00019_94RT | 045 | DJGUL00019_ | 94RT | DIGITAL |  | DJ01 | RELE AUXILIAR TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00019_79BS | 045 | DJGUL00019_ | 79BS | DIGITAL |  | DJ01 | 79 RELIG AUTOMATICO | NORMAL;BEM SUCEDIDA;; | 0;1;2;3 | NORMAL | BEM SUCEDIDA |  |  | Discrete | Single-Bit
045DJGUL00019_079C | 045 | DJGUL00019_ | 079C | DIGITAL |  | DJ01 | 79 RELIG AUTOMATICO | NORMAL;EM CURSO;; | 0;1;2;3 | NORMAL | EM CURSO |  |  | Discrete | Single-Bit | 12 |  |  | BRK_045DJGUL00019
045DJGUL00019_79MS | 045 | DJGUL00019_ | 79MS | DIGITAL |  | DJ01 | 79 RELIG AUTOMATICO | NORMAL;MAL SUCEDIDA;; | 0;1;2;3 | NORMAL | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 13 |  |  | BRK_045DJGUL00019
045DJGUL00019_AJCG | 045 | DJGUL00019_ | AJCG | DIGITAL | N2= ELIPSE | DJ01 | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO;2;3 | 0;1;2;3 | NORMAL | ALTERADO
045DJGUL00019_00DF | 045 | DJGUL00019_ | 00DF | DIGITAL |  | DJ01 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;2;3 | 0;1;2;3 | NORMAL | DEFEITO
045DJGUL00019_00LR | 045 | DJGUL00019_ | 00LR | DIGITAL |  | DJ01 | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;2;3 | 1;0;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 15 |  |  | BRK_045DJGUL00019
045DJGUL00019_NMFL | 045 | DJGUL00019_ | NMFL | DIGITAL |  | DJ01 | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;2;3 | 0;1;2;3 | NORMAL | FALHA |  |  |  |  | N2
045DJGUL00019_51QT | 045 | DJGUL00019_ | 51QT | DIGITAL |  | DJ01 | 51 PROT SEQ NEGATIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00029_027I | 045 | DJGUL00029_ | 027I | DIGITAL |  | DJ02 | 27 PROT SUB TENSÃO | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 38 |  |  | BRK_045DJGUL00029_Multifuncional_PE
045DJGUL00029_50FA | 045 | DJGUL00029_ | 50FA | DIGITAL |  | DJ02 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 22 |  |  | BRK_045DJGUL00029_50_RS
045DJGUL00029_50FB | 045 | DJGUL00029_ | 50FB | DIGITAL |  | DJ02 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 23 |  |  | BRK_045DJGUL00029_50_RS
045DJGUL00029_50NE | 045 | DJGUL00029_ | 50NE | DIGITAL |  | DJ02 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 25 |  |  | BRK_045DJGUL00029_50N_RS
045DJGUL00029_50FV | 045 | DJGUL00029_ | 50FV | DIGITAL |  | DJ02 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 24 |  |  | BRK_045DJGUL00029_50_RS
045DJGUL00029_51FA | 045 | DJGUL00029_ | 51FA | DIGITAL |  | DJ02 | 51 PROT AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00029_51AP | 045 | DJGUL00029_ | 51AP | DIGITAL | N2= ELIPSE | DJ02 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00029_51FB | 045 | DJGUL00029_ | 51FB | DIGITAL |  | DJ02 | 51 PROT BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00029_51BP | 045 | DJGUL00029_ | 51BP | DIGITAL | N2= ELIPSE | DJ02 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00029_51NE | 045 | DJGUL00029_ | 51NE | DIGITAL |  | DJ02 | 51 PROT NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00029_51NP | 045 | DJGUL00029_ | 51NP | DIGITAL | N2= ELIPSE | DJ02 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00029_51FV | 045 | DJGUL00029_ | 51FV | DIGITAL |  | DJ02 | 51 PROT VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00029_51VP | 045 | DJGUL00029_ | 51VP | DIGITAL | N2= ELIPSE | DJ02 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00029_CBTL | 045 | DJGUL00029_ | CBTL | DIGITAL |  | DJ02 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;2;3 | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 34 |  |  | BRK_045DJGUL00029 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00029_0DPT | 045 | DJGUL00029_ | 0DPT | DIGITAL |  | DJ02 | 52 DISJ DESLIG PROTEÇÃO |  | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00029_SF61 | 045 | DJGUL00029_ | SF61 | DIGITAL |  | DJ02 | 52 DISJ SF6 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 124 |  |  | NORMAL;ALARME;;
045DJGUL00029_SF62 | 045 | DJGUL00029_ | SF62 | DIGITAL |  | DJ02 | 52 DISJ SF6 2º EST | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 156 |  |  | BRK_045DJGUL00029_Multifuncional_PE
045DJGUL00029_FLTC | 045 | DJGUL00029_ | FLTC | DIGITAL |  | DJ02 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 29 |  |  | BRK_045DJGUL00029
045DJGUL00029_O792 | 045 | DJGUL00029_ | O792 | DIGITAL |  | DJ02 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;2;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 40 |  |  | BRK_045DJGUL00029
045DJGUL00029_52BG | 045 | DJGUL00029_ | 52BG | DIGITAL |  | DJ02 | 52 DJ BLOQ GERAL | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 28 |  |  | BRK_045DJGUL00029_Multifuncional_PE
045DJGUL00029_INAT | 045 | DJGUL00029_ | INAT | DIGITAL | N2= ELIPSE | DJ02 | 52 INATIVIDADE |  | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00029_TADJ | 045 | DJGUL00029_ | TADJ | DIGITAL | N2= ELIPSE | DJ02 | 52 TEMPO ABERTURA |  | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00029_00TM | 045 | DJGUL00029_ | 00TM | DIGITAL | N2= ELIPSE | DJ02 | 52 TEMPO CARREGAR MOLA |  | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00029_TFDJ | 045 | DJGUL00029_ | TFDJ | DIGITAL | N2= ELIPSE | DJ02 | 52 TEMPO FECHAMENTO |  | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00029_00FD | 045 | DJGUL00029_ | 00FD | DIGITAL |  | DJ02 | 79 FALHA LIGAR DJ |  | 0;1;2;3 | NORMAL | ALARME
045DJGUL00029_OO79 | 045 | DJGUL00029_ | OO79 | COMANDO |  | DJ02 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 31 | Multibit | 2008;2007 | BRK_045DJGUL00029 | 79 RELIG AUTOMATICO INVERTIDO
45DJGUL00029_79BA | 045 | DJGUL00029_ | 79BA | DIGITAL |  | DJ02 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO
045DJGUL00029_00DF | 045 | DJGUL00029_ | 00DF | DIGITAL |  | DJ02 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 37 |  |  | BRK_045DJGUL00029
045DJGUL00029_0EST | 045 | DJGUL00029_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ02 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVALIDO | Discrete | Single-Bit | 26 | Multibit | 2005;2006 | BRK_045DJGUL00029
045DJGUL00029_DJTP | 045 | DJGUL00029_ | DJTP | DIGITAL |  | DJ02 | DISJUNTOR TP | ARMADO;DESARMADO;2;3 | 0;1;2;3 | ARMADO | DESARMADO
045DJGUL00029_UCGS | 045 | DJGUL00029_ | UCGS | DIGITAL |  | DJ02 | DISPARO PROTEÇÃO - COMUNICAÇÃO |  | 0;1;2;3 | NORMAL | FALHA
045DJGUL00029_MREQ | 045 | DJGUL00029_ | MREQ | DIGITAL | N2= ELIPSE | DJ02 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;2;3 | 0;1;2;3 | NORMAL | REQUERIDA
45DJGUL00019_94CT | 045 | DJGUL00029_ | 94CT | DIGITAL |  | DJ01 | RELE AUX. CORTA - TRIP | NORMAL;DEFEITO;2;3 | 0;1;2;3 | NORMAL | DEFEITO
45DJGUL00019_94T1 | 045 | DJGUL00029_ | 94T1 | DIGITAL | N2= ELIPSE | DJ01 | RELE AUX. CORTA - TRIP TR1 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
45DJGUL00019_94T2 | 045 | DJGUL00029_ | 94T2 | DIGITAL | N2= ELIPSE | DJ01 | RELE AUX. CORTA - TRIP TR2 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
45DJGUL00019_94T3 | 045 | DJGUL00029_ | 94T3 | DIGITAL | N2= ELIPSE | DJ01 | RELE AUX. CORTA - TRIP TR3 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
45DJGUL00019_94T4 | 045 | DJGUL00029_ | 94T4 | DIGITAL | N2= ELIPSE | DJ01 | RELE AUX. CORTA - TRIP TR4 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
45DJGUL00019_94RT | 045 | DJGUL00029_ | 94RT | DIGITAL |  | DJ01 | RELE AUXILIAR TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00029_79MS | 045 | DJGUL00029_ | 79MS | DIGITAL |  | DJ02 | 79 RELIG AUTOMATICO | NORMAL;MAL SUCEDIDA;; | 0;1;3;2 | NORMAL | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 33 |  |  | BRK_045DJGUL00029
045DJGUL00029_079C | 045 | DJGUL00029_ | 079C | DIGITAL |  | DJ02 | 79 RELIG AUTOMATICO | NORMAL;EM CURSO;; | 0;1;2;3 | NORMAL | EM CURSO |  |  | Discrete | Single-Bit | 32 |  |  | BRK_045DJGUL00029
045DJGUL00029_79BS | 045 | DJGUL00029_ | 79BS | DIGITAL |  | DJ02 | 79 RELIG AUTOMATICO | NORMAL;BEM SUCEDIDA;; | 0;1;3;2 | NORMAL | BEM SUCEDIDA |  |  | Discrete | Single-Bit
045DJGUL00029_AJCG | 045 | DJGUL00029_ | AJCG | DIGITAL | N2= ELIPSE | DJ02 | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO;2;3 | 0;1;2;3 | NORMAL | ALTERADO
045DJGUL00029_00LR | 045 | DJGUL00029_ | 00LR | DIGITAL |  | DJ02 | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;2;3 | 1;0;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 35 |  |  | BRK_045DJGUL00029
045DJGUL00029_NMFL | 045 | DJGUL00029_ | NMFL | DIGITAL |  | DJ02 | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;2;3 | 0;1;2;3 | NORMAL | FALHA |  |  | N2
045DJGUL00029_51QT | 045 | DJGUL00029_ | 51QT | DIGITAL |  | DJ02 | 51 PROT SEQ NEGATIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_50FA | 045 | DJGUL00039_ | 50FA | DIGITAL |  | SC11 (DJ03) | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00039_50FB | 045 | DJGUL00039_ | 50FB | DIGITAL |  | SC11 (DJ03) | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00039_50NE | 045 | DJGUL00039_ | 50NE | DIGITAL |  | SC11 (DJ03) | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50N_RS
045DJGUL00039_50FV | 045 | DJGUL00039_ | 50FV | DIGITAL |  | SC11 (DJ03) | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00039_51FA | 045 | DJGUL00039_ | 51FA | DIGITAL |  | SC11 (DJ03) | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00039_51FB | 045 | DJGUL00039_ | 51FB | DIGITAL |  | SC11 (DJ03) | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00039_51NE | 045 | DJGUL00039_ | 51NE | DIGITAL |  | SC11 (DJ03) | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51N_RS
045DJGUL00039_51FV | 045 | DJGUL00039_ | 51FV | DIGITAL |  | SC11 (DJ03) | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00039_CBTL | 045 | DJGUL00039_ | CBTL | DIGITAL |  | SC11 (DJ03) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00039_FLTC | 045 | DJGUL00039_ | FLTC | DIGITAL |  | SC11 (DJ03) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00039_52ML | 045 | DJGUL00039_ | 52ML | DIGITAL |  | SC11 (DJ03) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00039_00LR | 045 | DJGUL00039_ | 00LR | DIGITAL |  | SC11 (DJ03) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00039_861A | 045 | DJGUL00039_ | 861A | COMANDO |  | SC11 (DJ03) | 86 CR BA 1A | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit |  | Single-Bit | 2067 | BRK_045DJGUL00039_Multifuncional_PE
045DJGUL00039_861B | 045 | DJGUL00039_ | 861B | COMANDO |  | SC11 (DJ03) | 86 CR BA 1B | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit |  | Single-Bit | 2233 | BRK_045DJGUL00039_Multifuncional_PE
045DJGUL00039_DB1A | 045 | DJGUL00039_ | DB1A | DIGITAL |  | SC11 (DJ03) | 86 CIRC ABER CR BA 1A | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00039_DB1B | 045 | DJGUL00039_ | DB1B | DIGITAL |  | SC11 (DJ03) | 86 CIRC ABER CR BA 1B | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00039_BAIS | 045 | DJGUL00039_ | BAIS | DIGITAL |  | SC11 (DJ03) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00039_00DF | 045 | DJGUL00039_ | 00DF | DIGITAL |  | SC11 (DJ03) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00039_0EST | 045 | DJGUL00039_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SC11 (DJ03) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVÁLIDO | Discrete | Single-Bit |  | Multibit | 2065;2066 | BRK_045DJGUL00039 | 0EST DIGITAL SIMPLES
045DJGUL00039_DJTP | 045 | DJGUL00039_ | DJTP | DIGITAL |  | SC11 (DJ03) | DISJUNTOR TP | ARMADO;DESARMADO;0;3 | 0;1;2;3 | ARMADO | DESARMADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039 | DISJUNTOR TP
045DJGUL00039_027I | 045 | DJGUL00039_ | 027I | DIGITAL |  | SC11 (DJ03) | 27 PROT SUB TENSÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_50SL | 045 | DJGUL00039_ | 50SL | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 50 SELETIVIDADE LOGICA | NORMAL;BLOQUEADO;; | 0;1;2;3 | NORMAL | BLOQUEADO
045DJGUL00039_51AP | 045 | DJGUL00039_ | 51AP | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00039_51BP | 045 | DJGUL00039_ | 51BP | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00039_51NP | 045 | DJGUL00039_ | 51NP | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00039_51VP | 045 | DJGUL00039_ | 51VP | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00039_NMFL | 045 | DJGUL00039_ | NMFL | DIGITAL |  | SC11 (DJ03) | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_52BF | 045 | DJGUL00039_ | 52BF | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00039_0DPT | 045 | DJGUL00039_ | 0DPT | DIGITAL |  | SC11 (DJ03) | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_FLTC | 045 | DJGUL00039_ | FLTC | DIGITAL |  | SC11 (DJ03) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00039_TADJ | 045 | DJGUL00039_ | TADJ | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00039_00TM | 045 | DJGUL00039_ | 00TM | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00039_TFDJ | 045 | DJGUL00039_ | TFDJ | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00039_E811 | 045 | DJGUL00039_ | E811 | DIGITAL |  | SC11 (DJ03) | 81 - ERAC 1º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00039_E812 | 045 | DJGUL00039_ | E812 | DIGITAL |  | SC11 (DJ03) | 81 - ERAC 2º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00039_E813 | 045 | DJGUL00039_ | E813 | DIGITAL |  | SC11 (DJ03) | 81 - ERAC 3º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00039_E814 | 045 | DJGUL00039_ | E814 | DIGITAL |  | SC11 (DJ03) | 81 - ERAC 4º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00039_E815 | 045 | DJGUL00039_ | E815 | DIGITAL |  | SC11 (DJ03) | 81 - ERAC 5º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00039_811E | 045 | DJGUL00039_ | 811E | DIGITAL |  | SC11 (DJ03) | 81 RL FREQ ERAC 1º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_812E | 045 | DJGUL00039_ | 812E | DIGITAL |  | SC11 (DJ03) | 81 RL FREQ ERAC 2º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_813E | 045 | DJGUL00039_ | 813E | DIGITAL |  | SC11 (DJ03) | 81 RL FREQ ERAC 3º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_814E | 045 | DJGUL00039_ | 814E | DIGITAL |  | SC11 (DJ03) | 81 RL FREQ ERAC 4º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_815E | 045 | DJGUL00039_ | 815E | DIGITAL |  | SC11 (DJ03) | 81 RL FREQ ERAC 5º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_081B | 045 | DJGUL00039_ | 081B | COMANDO |  | SC11 (DJ03) | 81 RL FREQUENCIA | NORMAL;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00039_081P | 045 | DJGUL00039_ | 081P | DIGITAL | N2= ELIPSE | SC11 (DJ03) | 81 RL FREQUENCIA | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00039_0EXT | 045 | DJGUL00039_ | 0EXT | DIGITAL |  | SC11 (DJ03) | DISJUNTOR | INSERIDO;EXTRAIDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00039_UCGS | 045 | DJGUL00039_ | UCGS | DIGITAL |  | SC11 (DJ03) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00039_MREQ | 045 | DJGUL00039_ | MREQ | DIGITAL | N2= ELIPSE | SC11 (DJ03) | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;2;3 | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00039_AFDD | 045 | DJGUL00039_ | AFDD | DIGITAL |  | SC11 (DJ03) | PROT ARCO - COMPARTIMENTO CABOS - SECUNDARIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_AJCG | 045 | DJGUL00039_ | AJCG | DIGITAL | N2= ELIPSE | SC11 (DJ03) | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO;; | 0;1;2;3 | NORMAL | ALTERADO
045DJGUL00039_NMFL | 045 | DJGUL00039_ | NMFL | DIGITAL |  | SC11 (DJ03) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00049_50FA | 045 | DJGUL00049_ | 50FA | DIGITAL |  | SC12 (DJ04) | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00049_50FB | 045 | DJGUL00049_ | 50FB | DIGITAL |  | SC12 (DJ04) | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00049_50NE | 045 | DJGUL00049_ | 50NE | DIGITAL |  | SC12 (DJ04) | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50N_RS
045DJGUL00049_50FV | 045 | DJGUL00049_ | 50FV | DIGITAL |  | SC12 (DJ04) | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00049_51FA | 045 | DJGUL00049_ | 51FA | DIGITAL |  | SC12 (DJ04) | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00049_51FB | 045 | DJGUL00049_ | 51FB | DIGITAL |  | SC12 (DJ04) | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00049_51NE | 045 | DJGUL00049_ | 51NE | DIGITAL |  | SC12 (DJ04) | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51N_RS
045DJGUL00049_51FV | 045 | DJGUL00049_ | 51FV | DIGITAL |  | SC12 (DJ04) | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00049_CBTL | 045 | DJGUL00049_ | CBTL | DIGITAL |  | SC12 (DJ04) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00049_FLTC | 045 | DJGUL00049_ | FLTC | DIGITAL |  | SC12 (DJ04) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_52ML | 045 | DJGUL00049_ | 52ML | DIGITAL |  | SC12 (DJ04) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_00LR | 045 | DJGUL00049_ | 00LR | DIGITAL |  | SC12 (DJ04) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_861A | 045 | DJGUL00049_ | 861A | COMANDO |  | SC12 (DJ04) | 86 CR BA 2A | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit |  | Single-Bit | 2067 | BRK_045DJGUL00039_Multifuncional_PE
045DJGUL00049_861B | 045 | DJGUL00049_ | 861B | COMANDO |  | SC12 (DJ04) | 86 CR BA 2B | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit |  | Single-Bit | 2233 | BRK_045DJGUL00039_Multifuncional_PE
045DJGUL00049_DB1A | 045 | DJGUL00049_ | DB1A | DIGITAL |  | SC12 (DJ04) | 86 CIRC ABER CR BA 2A | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_DB1B | 045 | DJGUL00049_ | DB1B | DIGITAL |  | SC12 (DJ04) | 86 CIRC ABER CR BA 2B | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_BAIS | 045 | DJGUL00049_ | BAIS | DIGITAL |  | SC12 (DJ04) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_00DF | 045 | DJGUL00049_ | 00DF | DIGITAL |  | SC12 (DJ04) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_0EST | 045 | DJGUL00049_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SC12 (DJ04) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVÁLIDO | Discrete | Single-Bit |  | Multibit | 2065;2066 | BRK_045DJGUL00039
045DJGUL00049_DJTP | 045 | DJGUL00049_ | DJTP | DIGITAL |  | SC12 (DJ04) | DISJUNTOR TP | ARMADO;DESARMADO;0;3 | 0;1;2;3 | ARMADO | DESARMADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_027I | 045 | DJGUL00049_ | 027I | DIGITAL |  | SC12 (DJ04) | 27 PROT SUB TENSÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_50SL | 045 | DJGUL00049_ | 50SL | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 50 SELETIVIDADE LOGICA | NORMAL;BLOQUEADO;; | 0;1;2;3 | NORMAL | BLOQUEADO
045DJGUL00049_51AP | 045 | DJGUL00049_ | 51AP | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00049_51BP | 045 | DJGUL00049_ | 51BP | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00049_51NP | 045 | DJGUL00049_ | 51NP | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00049_51VP | 045 | DJGUL00049_ | 51VP | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00049_NMFL | 045 | DJGUL00049_ | NMFL | DIGITAL |  | SC12 (DJ04) | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_52BF | 045 | DJGUL00049_ | 52BF | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00049_0DPT | 045 | DJGUL00049_ | 0DPT | DIGITAL |  | SC12 (DJ04) | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_FLTC | 045 | DJGUL00049_ | FLTC | DIGITAL |  | SC12 (DJ04) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00049_TADJ | 045 | DJGUL00049_ | TADJ | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00049_00TM | 045 | DJGUL00049_ | 00TM | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00049_TFDJ | 045 | DJGUL00049_ | TFDJ | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00049_E811 | 045 | DJGUL00049_ | E811 | DIGITAL |  | SC12 (DJ04) | 81 - ERAC 1º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00049_E812 | 045 | DJGUL00049_ | E812 | DIGITAL |  | SC12 (DJ04) | 81 - ERAC 2º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00049_E813 | 045 | DJGUL00049_ | E813 | DIGITAL |  | SC12 (DJ04) | 81 - ERAC 3º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00049_E814 | 045 | DJGUL00049_ | E814 | DIGITAL |  | SC12 (DJ04) | 81 - ERAC 4º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00049_E815 | 045 | DJGUL00049_ | E815 | DIGITAL |  | SC12 (DJ04) | 81 - ERAC 5º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00049_811E | 045 | DJGUL00049_ | 811E | DIGITAL |  | SC12 (DJ04) | 81 RL FREQ ERAC 1º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_812E | 045 | DJGUL00049_ | 812E | DIGITAL |  | SC12 (DJ04) | 81 RL FREQ ERAC 2º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_813E | 045 | DJGUL00049_ | 813E | DIGITAL |  | SC12 (DJ04) | 81 RL FREQ ERAC 3º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_814E | 045 | DJGUL00049_ | 814E | DIGITAL |  | SC12 (DJ04) | 81 RL FREQ ERAC 4º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_815E | 045 | DJGUL00049_ | 815E | DIGITAL |  | SC12 (DJ04) | 81 RL FREQ ERAC 5º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_081B | 045 | DJGUL00049_ | 081B | COMANDO |  | SC12 (DJ04) | 81 RL FREQUENCIA | NORMAL;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00049_081P | 045 | DJGUL00049_ | 081P | DIGITAL | N2= ELIPSE | SC12 (DJ04) | 81 RL FREQUENCIA | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00049_0EXT | 045 | DJGUL00049_ | 0EXT | DIGITAL |  | SC12 (DJ04) | DISJUNTOR | INSERIDO;EXTRAIDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00049_UCGS | 045 | DJGUL00049_ | UCGS | DIGITAL |  | SC12 (DJ04) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00049_MREQ | 045 | DJGUL00049_ | MREQ | DIGITAL | N2= ELIPSE | SC12 (DJ04) | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;2;3 | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00049_AFDD | 045 | DJGUL00049_ | AFDD | DIGITAL |  | SC12 (DJ04) | PROT ARCO - COMPARTIMENTO CABOS - SECUNDARIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_AJCG | 045 | DJGUL00049_ | AJCG | DIGITAL | N2= ELIPSE | SC12 (DJ04) | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO;; | 0;1;2;3 | NORMAL | ALTERADO
045DJGUL00049_NMFL | 045 | DJGUL00049_ | NMFL | DIGITAL |  | SC12 (DJ04) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00059_50FA | 045 | DJGUL00059_ | 50FA | DIGITAL |  | SC13 (DJ05) | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00059_50FB | 045 | DJGUL00059_ | 50FB | DIGITAL |  | SC13 (DJ05) | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00059_50NE | 045 | DJGUL00059_ | 50NE | DIGITAL |  | SC13 (DJ05) | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50N_RS
045DJGUL00059_50FV | 045 | DJGUL00059_ | 50FV | DIGITAL |  | SC13 (DJ05) | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00059_51FA | 045 | DJGUL00059_ | 51FA | DIGITAL |  | SC13 (DJ05) | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00059_51FB | 045 | DJGUL00059_ | 51FB | DIGITAL |  | SC13 (DJ05) | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00059_51NE | 045 | DJGUL00059_ | 51NE | DIGITAL |  | SC13 (DJ05) | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51N_RS
045DJGUL00059_51FV | 045 | DJGUL00059_ | 51FV | DIGITAL |  | SC13 (DJ05) | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00059_CBTL | 045 | DJGUL00059_ | CBTL | DIGITAL |  | SC13 (DJ05) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00059_FLTC | 045 | DJGUL00059_ | FLTC | DIGITAL |  | SC13 (DJ05) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00059_52ML | 045 | DJGUL00059_ | 52ML | DIGITAL |  | SC13 (DJ05) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00059_00LR | 045 | DJGUL00059_ | 00LR | DIGITAL |  | SC13 (DJ05) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00059_861A | 045 | DJGUL00059_ | 861A | COMANDO |  | SC13 (DJ05) | 86 CR BA 3 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit |  | Single-Bit | 2067 | BRK_045DJGUL00039_Multifuncional_PE
045DJGUL00059_DB1A | 045 | DJGUL00059_ | DB1A | DIGITAL |  | SC13 (DJ05) | 86 CIRC ABER CR BA 3 | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00059_BAIS | 045 | DJGUL00059_ | BAIS | DIGITAL |  | SC13 (DJ05) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00059_00DF | 045 | DJGUL00059_ | 00DF | DIGITAL |  | SC13 (DJ05) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00059_0EST | 045 | DJGUL00059_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SC13 (DJ05) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVÁLIDO | Discrete | Single-Bit |  | Multibit | 2065;2066 | BRK_045DJGUL00039
045DJGUL00059_DJTP | 045 | DJGUL00059_ | DJTP | DIGITAL |  | SC13 (DJ05) | DISJUNTOR TP | ARMADO;DESARMADO;0;3 | 0;1;2;3 | ARMADO | DESARMADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00059_027I | 045 | DJGUL00059_ | 027I | DIGITAL |  | SC13 (DJ05) | 27 PROT SUB TENSÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_50SL | 045 | DJGUL00059_ | 50SL | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 50 SELETIVIDADE LOGICA | NORMAL;BLOQUEADO;; | 0;1;2;3 | NORMAL | BLOQUEADO
045DJGUL00059_51AP | 045 | DJGUL00059_ | 51AP | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00059_51BP | 045 | DJGUL00059_ | 51BP | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00059_51NP | 045 | DJGUL00059_ | 51NP | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00059_51VP | 045 | DJGUL00059_ | 51VP | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00059_NMFL | 045 | DJGUL00059_ | NMFL | DIGITAL |  | SC13 (DJ05) | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_52BF | 045 | DJGUL00059_ | 52BF | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00059_0DPT | 045 | DJGUL00059_ | 0DPT | DIGITAL |  | SC13 (DJ05) | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_FLTC | 045 | DJGUL00059_ | FLTC | DIGITAL |  | SC13 (DJ05) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00059_TADJ | 045 | DJGUL00059_ | TADJ | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00059_00TM | 045 | DJGUL00059_ | 00TM | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00059_TFDJ | 045 | DJGUL00059_ | TFDJ | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00059_E811 | 045 | DJGUL00059_ | E811 | DIGITAL |  | SC13 (DJ05) | 81 - ERAC 1º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00059_E812 | 045 | DJGUL00059_ | E812 | DIGITAL |  | SC13 (DJ05) | 81 - ERAC 2º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00059_E813 | 045 | DJGUL00059_ | E813 | DIGITAL |  | SC13 (DJ05) | 81 - ERAC 3º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00059_E814 | 045 | DJGUL00059_ | E814 | DIGITAL |  | SC13 (DJ05) | 81 - ERAC 4º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00059_E815 | 045 | DJGUL00059_ | E815 | DIGITAL |  | SC13 (DJ05) | 81 - ERAC 5º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00059_811E | 045 | DJGUL00059_ | 811E | DIGITAL |  | SC13 (DJ05) | 81 RL FREQ ERAC 1º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_812E | 045 | DJGUL00059_ | 812E | DIGITAL |  | SC13 (DJ05) | 81 RL FREQ ERAC 2º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_813E | 045 | DJGUL00059_ | 813E | DIGITAL |  | SC13 (DJ05) | 81 RL FREQ ERAC 3º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_814E | 045 | DJGUL00059_ | 814E | DIGITAL |  | SC13 (DJ05) | 81 RL FREQ ERAC 4º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_815E | 045 | DJGUL00059_ | 815E | DIGITAL |  | SC13 (DJ05) | 81 RL FREQ ERAC 5º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_081B | 045 | DJGUL00059_ | 081B | COMANDO |  | SC13 (DJ05) | 81 RL FREQUENCIA | NORMAL;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00059_081P | 045 | DJGUL00059_ | 081P | DIGITAL | N2= ELIPSE | SC13 (DJ05) | 81 RL FREQUENCIA | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00059_0EXT | 045 | DJGUL00059_ | 0EXT | DIGITAL |  | SC13 (DJ05) | DISJUNTOR | INSERIDO;EXTRAIDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00059_UCGS | 045 | DJGUL00059_ | UCGS | DIGITAL |  | SC13 (DJ05) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00059_MREQ | 045 | DJGUL00059_ | MREQ | DIGITAL | N2= ELIPSE | SC13 (DJ05) | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;2;3 | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00059_AFDD | 045 | DJGUL00059_ | AFDD | DIGITAL |  | SC13 (DJ05) | PROT ARCO - COMPARTIMENTO CABOS - SECUNDARIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_AJCG | 045 | DJGUL00059_ | AJCG | DIGITAL | N2= ELIPSE | SC13 (DJ05) | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO;; | 0;1;2;3 | NORMAL | ALTERADO
045DJGUL00059_NMFL | 045 | DJGUL00059_ | NMFL | DIGITAL |  | SC13 (DJ05) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00069_50FA | 045 | DJGUL00069_ | 50FA | DIGITAL |  | SC14 (DJ06) | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00069_50FB | 045 | DJGUL00069_ | 50FB | DIGITAL |  | SC14 (DJ06) | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00069_50NE | 045 | DJGUL00069_ | 50NE | DIGITAL |  | SC14 (DJ06) | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50N_RS
045DJGUL00069_50FV | 045 | DJGUL00069_ | 50FV | DIGITAL |  | SC14 (DJ06) | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_50_RS
045DJGUL00069_51FA | 045 | DJGUL00069_ | 51FA | DIGITAL |  | SC14 (DJ06) | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00069_51FB | 045 | DJGUL00069_ | 51FB | DIGITAL |  | SC14 (DJ06) | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00069_51NE | 045 | DJGUL00069_ | 51NE | DIGITAL |  | SC14 (DJ06) | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51N_RS
045DJGUL00069_51FV | 045 | DJGUL00069_ | 51FV | DIGITAL |  | SC14 (DJ06) | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039_51_RS
045DJGUL00069_CBTL | 045 | DJGUL00069_ | CBTL | DIGITAL |  | SC14 (DJ06) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00069_FLTC | 045 | DJGUL00069_ | FLTC | DIGITAL |  | SC14 (DJ06) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00069_52ML | 045 | DJGUL00069_ | 52ML | DIGITAL |  | SC14 (DJ06) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00069_00LR | 045 | DJGUL00069_ | 00LR | DIGITAL |  | SC14 (DJ06) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00069_861A | 045 | DJGUL00069_ | 861A | COMANDO |  | SC14 (DJ06) | 86 CR BA 4 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit |  | Single-Bit | 2067 | BRK_045DJGUL00039_Multifuncional_PE
045DJGUL00069_DB1A | 045 | DJGUL00069_ | DB1A | DIGITAL |  | SC14 (DJ06) | 86 CIRC ABER CR BA 4 | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00069_BAIS | 045 | DJGUL00069_ | BAIS | DIGITAL |  | SC14 (DJ06) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00069_00DF | 045 | DJGUL00069_ | 00DF | DIGITAL |  | SC14 (DJ06) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00069_0EST | 045 | DJGUL00069_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | SC14 (DJ06) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVÁLIDO | Discrete | Single-Bit |  | Multibit | 2065;2066 | BRK_045DJGUL00039
045DJGUL00069_DJTP | 045 | DJGUL00069_ | DJTP | DIGITAL |  | SC14 (DJ06) | DISJUNTOR TP | ARMADO;DESARMADO;0;3 | 0;1;2;3 | ARMADO | DESARMADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00069_027I | 045 | DJGUL00069_ | 027I | DIGITAL |  | SC14 (DJ06) | 27 PROT SUB TENSÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_50SL | 045 | DJGUL00069_ | 50SL | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 50 SELETIVIDADE LOGICA | NORMAL;BLOQUEADO;; | 0;1;2;3 | NORMAL | BLOQUEADO
045DJGUL00069_51AP | 045 | DJGUL00069_ | 51AP | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00069_51BP | 045 | DJGUL00069_ | 51BP | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00069_51NP | 045 | DJGUL00069_ | 51NP | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00069_51VP | 045 | DJGUL00069_ | 51VP | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00069_NMFL | 045 | DJGUL00069_ | NMFL | DIGITAL |  | SC14 (DJ06) | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_52BF | 045 | DJGUL00069_ | 52BF | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00069_0DPT | 045 | DJGUL00069_ | 0DPT | DIGITAL |  | SC14 (DJ06) | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_FLTC | 045 | DJGUL00069_ | FLTC | DIGITAL |  | SC14 (DJ06) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00069_TADJ | 045 | DJGUL00069_ | TADJ | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00069_00TM | 045 | DJGUL00069_ | 00TM | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00069_TFDJ | 045 | DJGUL00069_ | TFDJ | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00069_E811 | 045 | DJGUL00069_ | E811 | DIGITAL |  | SC14 (DJ06) | 81 - ERAC 1º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00069_E812 | 045 | DJGUL00069_ | E812 | DIGITAL |  | SC14 (DJ06) | 81 - ERAC 2º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00069_E813 | 045 | DJGUL00069_ | E813 | DIGITAL |  | SC14 (DJ06) | 81 - ERAC 3º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00069_E814 | 045 | DJGUL00069_ | E814 | DIGITAL |  | SC14 (DJ06) | 81 - ERAC 4º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00069_E815 | 045 | DJGUL00069_ | E815 | DIGITAL |  | SC14 (DJ06) | 81 - ERAC 5º ESTAGIO | NORMAL;ATIVO;; | 0;1;2;3 | DESATIVADO | ATIVO
045DJGUL00069_811E | 045 | DJGUL00069_ | 811E | DIGITAL |  | SC14 (DJ06) | 81 RL FREQ ERAC 1º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_812E | 045 | DJGUL00069_ | 812E | DIGITAL |  | SC14 (DJ06) | 81 RL FREQ ERAC 2º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_813E | 045 | DJGUL00069_ | 813E | DIGITAL |  | SC14 (DJ06) | 81 RL FREQ ERAC 3º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_814E | 045 | DJGUL00069_ | 814E | DIGITAL |  | SC14 (DJ06) | 81 RL FREQ ERAC 4º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_815E | 045 | DJGUL00069_ | 815E | DIGITAL |  | SC14 (DJ06) | 81 RL FREQ ERAC 5º ESTAGIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_081B | 045 | DJGUL00069_ | 081B | COMANDO |  | SC14 (DJ06) | 81 RL FREQUENCIA | NORMAL;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00069_081P | 045 | DJGUL00069_ | 081P | DIGITAL | N2= ELIPSE | SC14 (DJ06) | 81 RL FREQUENCIA | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00069_0EXT | 045 | DJGUL00069_ | 0EXT | DIGITAL |  | SC14 (DJ06) | DISJUNTOR | INSERIDO;EXTRAIDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00069_UCGS | 045 | DJGUL00069_ | UCGS | DIGITAL |  | SC14 (DJ06) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00069_MREQ | 045 | DJGUL00069_ | MREQ | DIGITAL | N2= ELIPSE | SC14 (DJ06) | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;2;3 | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00069_AFDD | 045 | DJGUL00069_ | AFDD | DIGITAL |  | SC14 (DJ06) | PROT ARCO - COMPARTIMENTO CABOS - SECUNDARIO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_AJCG | 045 | DJGUL00069_ | AJCG | DIGITAL | N2= ELIPSE | SC14 (DJ06) | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO;; | 0;1;2;3 | NORMAL | ALTERADO
045DJGUL00069_NMFL | 045 | DJGUL00069_ | NMFL | DIGITAL |  | SC14 (DJ06) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00109_CBTL | 045 | DJGUL00109_ | CBTL | DIGITAL |  | IT10 (DJ10) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109 | 52 CH BLOQ TELECOMANDO
045DJGUL00109_FLTC | 045 | DJGUL00109_ | FLTC | DIGITAL |  | IT10 (DJ10) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00109_52ML | 045 | DJGUL00109_ | 52ML | DIGITAL |  | IT10 (DJ10) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00109_BAIS | 045 | DJGUL00109_ | BAIS | DIGITAL |  | IT10 (DJ10) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00109_0EST | 045 | DJGUL00109_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | IT10 (DJ10) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVALIDO | Discrete | Double-Bit |  | Multibit | 2077;2078 | BRK_045DJGUL00109
045DJGUL00109_FLTC | 045 | DJGUL00109_ | FLTC | DIGITAL |  | IT10 (DJ10) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00109_0EXT | 045 | DJGUL00109_ | 0EXT | DIGITAL |  | IT10 (DJ10) | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00109_UCGS | 045 | DJGUL00109_ | UCGS | DIGITAL |  | IT10 (DJ10) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00109_00DF | 045 | DJGUL00109_ | 00DF | DIGITAL |  | IT10 (DJ10) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGUL00109_00LR | 045 | DJGUL00109_ | 00LR | DIGITAL |  | IT10 (DJ10) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO
045DJGUL00109_NMFL | 045 | DJGUL00109_ | NMFL | DIGITAL |  | IT10 (DJ10) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00119_50FA | 045 | DJGUL00119_ | 50FA | DIGITAL |  | DJ11 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00119_50FB | 045 | DJGUL00119_ | 50FB | DIGITAL |  | DJ11 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00119_50NE | 045 | DJGUL00119_ | 50NE | DIGITAL |  | DJ11 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00119_50FV | 045 | DJGUL00119_ | 50FV | DIGITAL |  | DJ11 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00119_51AP | 045 | DJGUL00119_ | 51AP | DIGITAL | N2= ELIPSE | DJ11 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00119_51FA | 045 | DJGUL00119_ | 51FA | DIGITAL |  | DJ11 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00119_51BP | 045 | DJGUL00119_ | 51BP | DIGITAL | N2= ELIPSE | DJ11 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA |  |  |  |  | N2
045DJGUL00119_51FB | 045 | DJGUL00119_ | 51FB | DIGITAL |  | DJ11 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00119_51NP | 045 | DJGUL00119_ | 51NP | DIGITAL | N2= ELIPSE | DJ11 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA |  |  |  |  | N2
045DJGUL00119_51NE | 045 | DJGUL00119_ | 51NE | DIGITAL |  | DJ11 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00119_51VP | 045 | DJGUL00119_ | 51VP | DIGITAL | N2= ELIPSE | DJ11 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00119_51FV | 045 | DJGUL00119_ | 51FV | DIGITAL |  | DJ11 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00119_51NB | 045 | DJGUL00119_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ11 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00119_NMFL | 045 | DJGUL00119_ | NMFL | DIGITAL |  | DJ11 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_52BF | 045 | DJGUL00119_ | 52BF | DIGITAL | N2= ELIPSE | DJ11 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00119_CBTL | 045 | DJGUL00119_ | CBTL | DIGITAL |  | DJ11 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139
045DJGUL00119_8612 | 045 | DJGUL00119_ | 8612 | DIGITAL | N2= ELIPSE | DJ11 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00119_LVAB | 045 | DJGUL00119_ | LVAB | DIGITAL |  | DJ11 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_0DPT | 045 | DJGUL00119_ | 0DPT | DIGITAL |  | DJ11 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_52ML | 045 | DJGUL00119_ | 52ML | DIGITAL |  | DJ11 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00119_BAIS | 045 | DJGUL00119_ | BAIS | DIGITAL |  | DJ11 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00119_TADJ | 045 | DJGUL00119_ | TADJ | DIGITAL | N2= ELIPSE | DJ11 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00119_00TM | 045 | DJGUL00119_ | 00TM | DIGITAL | N2= ELIPSE | DJ11 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00119_TFDJ | 045 | DJGUL00119_ | TFDJ | DIGITAL | N2= ELIPSE | DJ11 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00119_FLTC | 045 | DJGUL00119_ | FLTC | DIGITAL |  | DJ11 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00119_O791 | 045 | DJGUL00119_ | O791 | DIGITAL |  | DJ11 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00119_O792 | 045 | DJGUL00119_ | O792 | DIGITAL |  | DJ11 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00119_00FD | 045 | DJGUL00119_ | 00FD | DIGITAL |  | DJ11 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00119_79BP | 045 | DJGUL00119_ | 79BP | DIGITAL |  | DJ11 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00119_OO79 | 045 | DJGUL00119_ | OO79 | COMANDO / DIGITAL |  | DJ11 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00119_CHVS | 045 | DJGUL00119_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ11 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00119_0EXT | 045 | DJGUL00119_ | 0EXT | DIGITAL |  | DJ11 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00119_0EST | 045 | DJGUL00119_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ11 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00119_027G | 045 | DJGUL00119_ | 027G | DIGITAL | N2= ELIPSE | DJ11 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00119_UCGS | 045 | DJGUL00119_ | UCGS | DIGITAL |  | DJ11 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00119_AJM1 | 045 | DJGUL00119_ | AJM1 | DIGITAL |  | DJ11 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00119_AJM2 | 045 | DJGUL00119_ | AJM2 | DIGITAL |  | DJ11 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00119_AJM3 | 045 | DJGUL00119_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ11 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00119_LVVA | 045 | DJGUL00119_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ11 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00119_MREQ | 045 | DJGUL00119_ | MREQ | DIGITAL | N2= ELIPSE | DJ11 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00119_IATA | 045 | DJGUL00119_ | IATA | DIGITAL |  | DJ11 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_IATB | 045 | DJGUL00119_ | IATB | DIGITAL |  | DJ11 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_IATN | 045 | DJGUL00119_ | IATN | DIGITAL |  | DJ11 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_IATV | 045 | DJGUL00119_ | IATV | DIGITAL |  | DJ11 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_55SB | 045 | DJGUL00119_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ11 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00119_0REC | 045 | DJGUL00119_ | 0REC | DIGITAL | N2= ELIPSE | DJ11 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00119_REAQ | 045 | DJGUL00119_ | REAQ | DIGITAL | N2= ELIPSE | DJ11 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00119_551S | 045 | DJGUL00119_ | 551S | DIGITAL |  | DJ11 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_00SS | 045 | DJGUL00119_ | 00SS | DIGITAL |  | DJ11 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_027G | 045 | DJGUL00119_ | 027G | DIGITAL | N2= ELIPSE | DJ11 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00119_00LR | 045 | DJGUL00119_ | 00LR | DIGITAL |  | DJ11 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00119_00DF | 045 | DJGUL00119_ | 00DF | DIGITAL |  | DJ11 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00129_50FA | 045 | DJGUL00129_ | 50FA | DIGITAL |  | DJ12 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00129_50FB | 045 | DJGUL00129_ | 50FB | DIGITAL |  | DJ12 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00129_50NE | 045 | DJGUL00129_ | 50NE | DIGITAL |  | DJ12 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00129_50FV | 045 | DJGUL00129_ | 50FV | DIGITAL |  | DJ12 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00129_51AP | 045 | DJGUL00129_ | 51AP | DIGITAL | N2= ELIPSE | DJ12 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00129_51FA | 045 | DJGUL00129_ | 51FA | DIGITAL |  | DJ12 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00129_51BP | 045 | DJGUL00129_ | 51BP | DIGITAL | N2= ELIPSE | DJ12 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00129_51FB | 045 | DJGUL00129_ | 51FB | DIGITAL |  | DJ12 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00129_51NP | 045 | DJGUL00129_ | 51NP | DIGITAL | N2= ELIPSE | DJ12 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00129_51NE | 045 | DJGUL00129_ | 51NE | DIGITAL |  | DJ12 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00129_51VP | 045 | DJGUL00129_ | 51VP | DIGITAL | N2= ELIPSE | DJ12 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00129_51FV | 045 | DJGUL00129_ | 51FV | DIGITAL |  | DJ12 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00129_51NB | 045 | DJGUL00129_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ12 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00129_NMFL | 045 | DJGUL00129_ | NMFL | DIGITAL |  | DJ12 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_52BF | 045 | DJGUL00129_ | 52BF | DIGITAL | N2= ELIPSE | DJ12 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00129_CBTL | 045 | DJGUL00129_ | CBTL | DIGITAL |  | DJ12 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00129_8612 | 045 | DJGUL00129_ | 8612 | DIGITAL | N2= ELIPSE | DJ12 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00129_LVAB | 045 | DJGUL00129_ | LVAB | DIGITAL |  | DJ12 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_0DPT | 045 | DJGUL00129_ | 0DPT | DIGITAL |  | DJ12 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_52ML | 045 | DJGUL00129_ | 52ML | DIGITAL |  | DJ12 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00129_BAIS | 045 | DJGUL00129_ | BAIS | DIGITAL |  | DJ12 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00129_TADJ | 045 | DJGUL00129_ | TADJ | DIGITAL | N2= ELIPSE | DJ12 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00129_00TM | 045 | DJGUL00129_ | 00TM | DIGITAL | N2= ELIPSE | DJ12 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00129_TFDJ | 045 | DJGUL00129_ | TFDJ | DIGITAL | N2= ELIPSE | DJ12 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00129_FLTC | 045 | DJGUL00129_ | FLTC | DIGITAL |  | DJ12 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00129_O791 | 045 | DJGUL00129_ | O791 | DIGITAL |  | DJ12 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00129_O792 | 045 | DJGUL00129_ | O792 | DIGITAL |  | DJ12 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00129_00FD | 045 | DJGUL00129_ | 00FD | DIGITAL |  | DJ12 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00129_79BP | 045 | DJGUL00129_ | 79BP | DIGITAL |  | DJ12 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00129_OO79 | 045 | DJGUL00129_ | OO79 | COMANDO / DIGITAL |  | DJ12 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00129_CHVS | 045 | DJGUL00129_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ12 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00129_0EXT | 045 | DJGUL00129_ | 0EXT | DIGITAL |  | DJ12 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00129_0EST | 045 | DJGUL00129_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ12 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00129_027G | 045 | DJGUL00129_ | 027G | DIGITAL | N2= ELIPSE | DJ12 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00129_UCGS | 045 | DJGUL00129_ | UCGS | DIGITAL |  | DJ12 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00129_AJM1 | 045 | DJGUL00129_ | AJM1 | DIGITAL |  | DJ12 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00129_AJM2 | 045 | DJGUL00129_ | AJM2 | DIGITAL |  | DJ12 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00129_AJM3 | 045 | DJGUL00129_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ12 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00129_LVVA | 045 | DJGUL00129_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ12 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00129_MREQ | 045 | DJGUL00129_ | MREQ | DIGITAL | N2= ELIPSE | DJ12 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00129_IATA | 045 | DJGUL00129_ | IATA | DIGITAL |  | DJ12 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_IATB | 045 | DJGUL00129_ | IATB | DIGITAL |  | DJ12 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_IATN | 045 | DJGUL00129_ | IATN | DIGITAL |  | DJ12 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_IATV | 045 | DJGUL00129_ | IATV | DIGITAL |  | DJ12 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_55SB | 045 | DJGUL00129_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ12 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00129_0REC | 045 | DJGUL00129_ | 0REC | DIGITAL | N2= ELIPSE | DJ12 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00129_REAQ | 045 | DJGUL00129_ | REAQ | DIGITAL | N2= ELIPSE | DJ12 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00129_551S | 045 | DJGUL00129_ | 551S | DIGITAL |  | DJ12 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_00SS | 045 | DJGUL00129_ | 00SS | DIGITAL |  | DJ12 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_027G | 045 | DJGUL00129_ | 027G | DIGITAL | N2= ELIPSE | DJ12 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00129_00LR | 045 | DJGUL00129_ | 00LR | DIGITAL |  | DJ12 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00129_00DF | 045 | DJGUL00129_ | 00DF | DIGITAL |  | DJ12 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00139_50FA | 045 | DJGUL00139_ | 50FA | DIGITAL |  | DJ13 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00139_50FB | 045 | DJGUL00139_ | 50FB | DIGITAL |  | DJ13 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00139_50NE | 045 | DJGUL00139_ | 50NE | DIGITAL |  | DJ13 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00139_50FV | 045 | DJGUL00139_ | 50FV | DIGITAL |  | DJ13 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00139_51AP | 045 | DJGUL00139_ | 51AP | DIGITAL | N2= ELIPSE | DJ13 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00139_51FA | 045 | DJGUL00139_ | 51FA | DIGITAL |  | DJ13 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00139_51BP | 045 | DJGUL00139_ | 51BP | DIGITAL | N2= ELIPSE | DJ13 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00139_51FB | 045 | DJGUL00139_ | 51FB | DIGITAL |  | DJ13 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00139_51NP | 045 | DJGUL00139_ | 51NP | DIGITAL | N2= ELIPSE | DJ13 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00139_51NE | 045 | DJGUL00139_ | 51NE | DIGITAL |  | DJ13 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00139_51VP | 045 | DJGUL00139_ | 51VP | DIGITAL | N2= ELIPSE | DJ13 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00139_51FV | 045 | DJGUL00139_ | 51FV | DIGITAL |  | DJ13 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00139_51NB | 045 | DJGUL00139_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ13 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00139_NMFL | 045 | DJGUL00139_ | NMFL | DIGITAL |  | DJ13 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_52BF | 045 | DJGUL00139_ | 52BF | DIGITAL | N2= ELIPSE | DJ13 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00139_CBTL | 045 | DJGUL00139_ | CBTL | DIGITAL |  | DJ13 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00139_8612 | 045 | DJGUL00139_ | 8612 | DIGITAL | N2= ELIPSE | DJ13 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00139_LVAB | 045 | DJGUL00139_ | LVAB | DIGITAL |  | DJ13 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_0DPT | 045 | DJGUL00139_ | 0DPT | DIGITAL |  | DJ13 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_52ML | 045 | DJGUL00139_ | 52ML | DIGITAL |  | DJ13 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00139_BAIS | 045 | DJGUL00139_ | BAIS | DIGITAL |  | DJ13 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00139_TADJ | 045 | DJGUL00139_ | TADJ | DIGITAL | N2= ELIPSE | DJ13 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00139_00TM | 045 | DJGUL00139_ | 00TM | DIGITAL | N2= ELIPSE | DJ13 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00139_TFDJ | 045 | DJGUL00139_ | TFDJ | DIGITAL | N2= ELIPSE | DJ13 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00139_FLTC | 045 | DJGUL00139_ | FLTC | DIGITAL |  | DJ13 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00139_O791 | 045 | DJGUL00139_ | O791 | DIGITAL |  | DJ13 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00139_O792 | 045 | DJGUL00139_ | O792 | DIGITAL |  | DJ13 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00139_00FD | 045 | DJGUL00139_ | 00FD | DIGITAL |  | DJ13 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00139_79BP | 045 | DJGUL00139_ | 79BP | DIGITAL |  | DJ13 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00139_OO79 | 045 | DJGUL00139_ | OO79 | COMANDO / DIGITAL |  | DJ13 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00139_CHVS | 045 | DJGUL00139_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ13 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00139_0EXT | 045 | DJGUL00139_ | 0EXT | DIGITAL |  | DJ13 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00139_0EST | 045 | DJGUL00139_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ13 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00139_027G | 045 | DJGUL00139_ | 027G | DIGITAL | N2= ELIPSE | DJ13 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00139_UCGS | 045 | DJGUL00139_ | UCGS | DIGITAL |  | DJ13 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00139_AJM1 | 045 | DJGUL00139_ | AJM1 | DIGITAL |  | DJ13 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00139_AJM2 | 045 | DJGUL00139_ | AJM2 | DIGITAL |  | DJ13 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00139_AJM3 | 045 | DJGUL00139_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ13 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00139_LVVA | 045 | DJGUL00139_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ13 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00139_MREQ | 045 | DJGUL00139_ | MREQ | DIGITAL | N2= ELIPSE | DJ13 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00139_IATA | 045 | DJGUL00139_ | IATA | DIGITAL |  | DJ13 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_IATB | 045 | DJGUL00139_ | IATB | DIGITAL |  | DJ13 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_IATN | 045 | DJGUL00139_ | IATN | DIGITAL |  | DJ13 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_IATV | 045 | DJGUL00139_ | IATV | DIGITAL |  | DJ13 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_55SB | 045 | DJGUL00139_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ13 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00139_0REC | 045 | DJGUL00139_ | 0REC | DIGITAL | N2= ELIPSE | DJ13 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00139_REAQ | 045 | DJGUL00139_ | REAQ | DIGITAL | N2= ELIPSE | DJ13 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00139_551S | 045 | DJGUL00139_ | 551S | DIGITAL |  | DJ13 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_00SS | 045 | DJGUL00139_ | 00SS | DIGITAL |  | DJ13 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_027G | 045 | DJGUL00139_ | 027G | DIGITAL | N2= ELIPSE | DJ13 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00139_00LR | 045 | DJGUL00139_ | 00LR | DIGITAL |  | DJ13 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00139_00DF | 045 | DJGUL00139_ | 00DF | DIGITAL |  | DJ13 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00139_AFDC | 045 | DJGUL00139_ | AFDC | DIGITAL |  | DJ13 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_50FA | 045 | DJGUL00149_ | 50FA | DIGITAL |  | DJ14 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00149_50FB | 045 | DJGUL00149_ | 50FB | DIGITAL |  | DJ14 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00149_50NE | 045 | DJGUL00149_ | 50NE | DIGITAL |  | DJ14 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00149_50FV | 045 | DJGUL00149_ | 50FV | DIGITAL |  | DJ14 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00149_51AP | 045 | DJGUL00149_ | 51AP | DIGITAL | N2= ELIPSE | DJ14 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00149_51FA | 045 | DJGUL00149_ | 51FA | DIGITAL |  | DJ14 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00149_51BP | 045 | DJGUL00149_ | 51BP | DIGITAL | N2= ELIPSE | DJ14 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00149_51FB | 045 | DJGUL00149_ | 51FB | DIGITAL |  | DJ14 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00149_51NP | 045 | DJGUL00149_ | 51NP | DIGITAL | N2= ELIPSE | DJ14 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00149_51NE | 045 | DJGUL00149_ | 51NE | DIGITAL |  | DJ14 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00149_51VP | 045 | DJGUL00149_ | 51VP | DIGITAL | N2= ELIPSE | DJ14 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00149_51FV | 045 | DJGUL00149_ | 51FV | DIGITAL |  | DJ14 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00149_51NB | 045 | DJGUL00149_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ14 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00149_NMFL | 045 | DJGUL00149_ | NMFL | DIGITAL |  | DJ14 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_52BF | 045 | DJGUL00149_ | 52BF | DIGITAL | N2= ELIPSE | DJ14 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00149_CBTL | 045 | DJGUL00149_ | CBTL | DIGITAL |  | DJ14 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00149_8612 | 045 | DJGUL00149_ | 8612 | DIGITAL | N2= ELIPSE | DJ14 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00149_LVAB | 045 | DJGUL00149_ | LVAB | DIGITAL |  | DJ14 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_0DPT | 045 | DJGUL00149_ | 0DPT | DIGITAL |  | DJ14 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_52ML | 045 | DJGUL00149_ | 52ML | DIGITAL |  | DJ14 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00149_BAIS | 045 | DJGUL00149_ | BAIS | DIGITAL |  | DJ14 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00149_TADJ | 045 | DJGUL00149_ | TADJ | DIGITAL | N2= ELIPSE | DJ14 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00149_00TM | 045 | DJGUL00149_ | 00TM | DIGITAL | N2= ELIPSE | DJ14 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00149_TFDJ | 045 | DJGUL00149_ | TFDJ | DIGITAL | N2= ELIPSE | DJ14 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00149_FLTC | 045 | DJGUL00149_ | FLTC | DIGITAL |  | DJ14 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00149_O791 | 045 | DJGUL00149_ | O791 | DIGITAL |  | DJ14 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00149_O792 | 045 | DJGUL00149_ | O792 | DIGITAL |  | DJ14 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00149_00FD | 045 | DJGUL00149_ | 00FD | DIGITAL |  | DJ14 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00149_79BP | 045 | DJGUL00149_ | 79BP | DIGITAL |  | DJ14 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00149_OO79 | 045 | DJGUL00149_ | OO79 | COMANDO / DIGITAL |  | DJ14 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00149_CHVS | 045 | DJGUL00149_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ14 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00149_0EXT | 045 | DJGUL00149_ | 0EXT | DIGITAL |  | DJ14 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00149_0EST | 045 | DJGUL00149_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ14 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00149_027G | 045 | DJGUL00149_ | 027G | DIGITAL | N2= ELIPSE | DJ14 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00149_UCGS | 045 | DJGUL00149_ | UCGS | DIGITAL |  | DJ14 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00149_AJM1 | 045 | DJGUL00149_ | AJM1 | DIGITAL |  | DJ14 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00149_AJM2 | 045 | DJGUL00149_ | AJM2 | DIGITAL |  | DJ14 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00149_AJM3 | 045 | DJGUL00149_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ14 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00149_LVVA | 045 | DJGUL00149_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ14 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00149_MREQ | 045 | DJGUL00149_ | MREQ | DIGITAL | N2= ELIPSE | DJ14 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00149_IATA | 045 | DJGUL00149_ | IATA | DIGITAL |  | DJ14 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_IATB | 045 | DJGUL00149_ | IATB | DIGITAL |  | DJ14 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_IATN | 045 | DJGUL00149_ | IATN | DIGITAL |  | DJ14 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_IATV | 045 | DJGUL00149_ | IATV | DIGITAL |  | DJ14 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_55SB | 045 | DJGUL00149_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ14 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00149_0REC | 045 | DJGUL00149_ | 0REC | DIGITAL | N2= ELIPSE | DJ14 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00149_REAQ | 045 | DJGUL00149_ | REAQ | DIGITAL | N2= ELIPSE | DJ14 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00149_551S | 045 | DJGUL00149_ | 551S | DIGITAL |  | DJ14 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_00SS | 045 | DJGUL00149_ | 00SS | DIGITAL |  | DJ14 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_027G | 045 | DJGUL00149_ | 027G | DIGITAL | N2= ELIPSE | DJ14 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00149_00LR | 045 | DJGUL00149_ | 00LR | DIGITAL |  | DJ14 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00149_00DF | 045 | DJGUL00149_ | 00DF | DIGITAL |  | DJ14 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00159_50FA | 045 | DJGUL00159_ | 50FA | DIGITAL |  | DJ15 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00159_50FB | 045 | DJGUL00159_ | 50FB | DIGITAL |  | DJ15 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00159_50NE | 045 | DJGUL00159_ | 50NE | DIGITAL |  | DJ15 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00159_50FV | 045 | DJGUL00159_ | 50FV | DIGITAL |  | DJ15 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00159_51AP | 045 | DJGUL00159_ | 51AP | DIGITAL | N2= ELIPSE | DJ15 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00159_51FA | 045 | DJGUL00159_ | 51FA | DIGITAL |  | DJ15 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00159_51BP | 045 | DJGUL00159_ | 51BP | DIGITAL | N2= ELIPSE | DJ15 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00159_51FB | 045 | DJGUL00159_ | 51FB | DIGITAL |  | DJ15 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00159_51NP | 045 | DJGUL00159_ | 51NP | DIGITAL | N2= ELIPSE | DJ15 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00159_51NE | 045 | DJGUL00159_ | 51NE | DIGITAL |  | DJ15 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00159_51VP | 045 | DJGUL00159_ | 51VP | DIGITAL | N2= ELIPSE | DJ15 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00159_51FV | 045 | DJGUL00159_ | 51FV | DIGITAL |  | DJ15 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00159_51NB | 045 | DJGUL00159_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ15 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00159_NMFL | 045 | DJGUL00159_ | NMFL | DIGITAL |  | DJ15 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_52BF | 045 | DJGUL00159_ | 52BF | DIGITAL | N2= ELIPSE | DJ15 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00159_CBTL | 045 | DJGUL00159_ | CBTL | DIGITAL |  | DJ15 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00159_8612 | 045 | DJGUL00159_ | 8612 | DIGITAL | N2= ELIPSE | DJ15 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00159_LVAB | 045 | DJGUL00159_ | LVAB | DIGITAL |  | DJ15 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_0DPT | 045 | DJGUL00159_ | 0DPT | DIGITAL |  | DJ15 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_52ML | 045 | DJGUL00159_ | 52ML | DIGITAL |  | DJ15 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00159_BAIS | 045 | DJGUL00159_ | BAIS | DIGITAL |  | DJ15 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00159_TADJ | 045 | DJGUL00159_ | TADJ | DIGITAL | N2= ELIPSE | DJ15 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00159_00TM | 045 | DJGUL00159_ | 00TM | DIGITAL | N2= ELIPSE | DJ15 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00159_TFDJ | 045 | DJGUL00159_ | TFDJ | DIGITAL | N2= ELIPSE | DJ15 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00159_FLTC | 045 | DJGUL00159_ | FLTC | DIGITAL |  | DJ15 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00159_O791 | 045 | DJGUL00159_ | O791 | DIGITAL |  | DJ15 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00159_O792 | 045 | DJGUL00159_ | O792 | DIGITAL |  | DJ15 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00159_00FD | 045 | DJGUL00159_ | 00FD | DIGITAL |  | DJ15 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00159_79BP | 045 | DJGUL00159_ | 79BP | DIGITAL |  | DJ15 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00159_OO79 | 045 | DJGUL00159_ | OO79 | COMANDO / DIGITAL |  | DJ15 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00159_CHVS | 045 | DJGUL00159_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ15 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00159_0EXT | 045 | DJGUL00159_ | 0EXT | DIGITAL |  | DJ15 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00159_0EST | 045 | DJGUL00159_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ15 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00159_027G | 045 | DJGUL00159_ | 027G | DIGITAL | N2= ELIPSE | DJ15 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00159_UCGS | 045 | DJGUL00159_ | UCGS | DIGITAL |  | DJ15 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00159_AJM1 | 045 | DJGUL00159_ | AJM1 | DIGITAL |  | DJ15 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00159_AJM2 | 045 | DJGUL00159_ | AJM2 | DIGITAL |  | DJ15 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00159_AJM3 | 045 | DJGUL00159_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ15 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00159_LVVA | 045 | DJGUL00159_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ15 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00159_MREQ | 045 | DJGUL00159_ | MREQ | DIGITAL | N2= ELIPSE | DJ15 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00159_IATA | 045 | DJGUL00159_ | IATA | DIGITAL |  | DJ15 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_IATB | 045 | DJGUL00159_ | IATB | DIGITAL |  | DJ15 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_IATN | 045 | DJGUL00159_ | IATN | DIGITAL |  | DJ15 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_IATV | 045 | DJGUL00159_ | IATV | DIGITAL |  | DJ15 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_55SB | 045 | DJGUL00159_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ15 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00159_0REC | 045 | DJGUL00159_ | 0REC | DIGITAL | N2= ELIPSE | DJ15 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00159_REAQ | 045 | DJGUL00159_ | REAQ | DIGITAL | N2= ELIPSE | DJ15 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00159_551S | 045 | DJGUL00159_ | 551S | DIGITAL |  | DJ15 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_00SS | 045 | DJGUL00159_ | 00SS | DIGITAL |  | DJ15 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_027G | 045 | DJGUL00159_ | 027G | DIGITAL | N2= ELIPSE | DJ15 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00159_00LR | 045 | DJGUL00159_ | 00LR | DIGITAL |  | DJ15 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00159_00DF | 045 | DJGUL00159_ | 00DF | DIGITAL |  | DJ15 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00169_50FA | 045 | DJGUL00169_ | 50FA | DIGITAL |  | DJ16 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00169_50FB | 045 | DJGUL00169_ | 50FB | DIGITAL |  | DJ16 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00169_50NE | 045 | DJGUL00169_ | 50NE | DIGITAL |  | DJ16 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00169_50FV | 045 | DJGUL00169_ | 50FV | DIGITAL |  | DJ16 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00169_51AP | 045 | DJGUL00169_ | 51AP | DIGITAL | N2= ELIPSE | DJ16 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00169_51FA | 045 | DJGUL00169_ | 51FA | DIGITAL |  | DJ16 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00169_51BP | 045 | DJGUL00169_ | 51BP | DIGITAL | N2= ELIPSE | DJ16 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00169_51FB | 045 | DJGUL00169_ | 51FB | DIGITAL |  | DJ16 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00169_51NP | 045 | DJGUL00169_ | 51NP | DIGITAL | N2= ELIPSE | DJ16 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00169_51NE | 045 | DJGUL00169_ | 51NE | DIGITAL |  | DJ16 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00169_51VP | 045 | DJGUL00169_ | 51VP | DIGITAL | N2= ELIPSE | DJ16 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00169_51FV | 045 | DJGUL00169_ | 51FV | DIGITAL |  | DJ16 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00169_51NB | 045 | DJGUL00169_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ16 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00169_NMFL | 045 | DJGUL00169_ | NMFL | DIGITAL |  | DJ16 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_52BF | 045 | DJGUL00169_ | 52BF | DIGITAL | N2= ELIPSE | DJ16 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00169_CBTL | 045 | DJGUL00169_ | CBTL | DIGITAL |  | DJ16 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00169_8612 | 045 | DJGUL00169_ | 8612 | DIGITAL | N2= ELIPSE | DJ16 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00169_LVAB | 045 | DJGUL00169_ | LVAB | DIGITAL |  | DJ16 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_0DPT | 045 | DJGUL00169_ | 0DPT | DIGITAL |  | DJ16 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_52ML | 045 | DJGUL00169_ | 52ML | DIGITAL |  | DJ16 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00169_BAIS | 045 | DJGUL00169_ | BAIS | DIGITAL |  | DJ16 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00169_TADJ | 045 | DJGUL00169_ | TADJ | DIGITAL | N2= ELIPSE | DJ16 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00169_00TM | 045 | DJGUL00169_ | 00TM | DIGITAL | N2= ELIPSE | DJ16 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00169_TFDJ | 045 | DJGUL00169_ | TFDJ | DIGITAL | N2= ELIPSE | DJ16 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00169_FLTC | 045 | DJGUL00169_ | FLTC | DIGITAL |  | DJ16 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00169_O791 | 045 | DJGUL00169_ | O791 | DIGITAL |  | DJ16 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00169_O792 | 045 | DJGUL00169_ | O792 | DIGITAL |  | DJ16 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00169_00FD | 045 | DJGUL00169_ | 00FD | DIGITAL |  | DJ16 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00169_79BP | 045 | DJGUL00169_ | 79BP | DIGITAL |  | DJ16 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00169_OO79 | 045 | DJGUL00169_ | OO79 | COMANDO / DIGITAL |  | DJ16 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00169_CHVS | 045 | DJGUL00169_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ16 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00169_0EXT | 045 | DJGUL00169_ | 0EXT | DIGITAL |  | DJ16 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00169_0EST | 045 | DJGUL00169_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ16 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00169_027G | 045 | DJGUL00169_ | 027G | DIGITAL | N2= ELIPSE | DJ16 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00169_UCGS | 045 | DJGUL00169_ | UCGS | DIGITAL |  | DJ16 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00169_AJM1 | 045 | DJGUL00169_ | AJM1 | DIGITAL |  | DJ16 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00169_AJM2 | 045 | DJGUL00169_ | AJM2 | DIGITAL |  | DJ16 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00169_AJM3 | 045 | DJGUL00169_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ16 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00169_LVVA | 045 | DJGUL00169_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ16 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00169_MREQ | 045 | DJGUL00169_ | MREQ | DIGITAL | N2= ELIPSE | DJ16 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00169_IATA | 045 | DJGUL00169_ | IATA | DIGITAL |  | DJ16 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_IATB | 045 | DJGUL00169_ | IATB | DIGITAL |  | DJ16 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_IATN | 045 | DJGUL00169_ | IATN | DIGITAL |  | DJ16 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_IATV | 045 | DJGUL00169_ | IATV | DIGITAL |  | DJ16 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_55SB | 045 | DJGUL00169_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ16 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00169_0REC | 045 | DJGUL00169_ | 0REC | DIGITAL | N2= ELIPSE | DJ16 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00169_REAQ | 045 | DJGUL00169_ | REAQ | DIGITAL | N2= ELIPSE | DJ16 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00169_551S | 045 | DJGUL00169_ | 551S | DIGITAL |  | DJ16 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_00SS | 045 | DJGUL00169_ | 00SS | DIGITAL |  | DJ16 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_027G | 045 | DJGUL00169_ | 027G | DIGITAL | N2= ELIPSE | DJ16 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00169_00LR | 045 | DJGUL00169_ | 00LR | DIGITAL |  | DJ16 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00169_00DF | 045 | DJGUL00169_ | 00DF | DIGITAL |  | DJ16 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00209_CBTL | 045 | DJGUL00209_ | CBTL | DIGITAL |  | IT20 (DJ20) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109 | 52 CH BLOQ TELECOMANDO
045DJGUL00209_FLTC | 045 | DJGUL00209_ | FLTC | DIGITAL |  | IT20 (DJ20) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00209_52ML | 045 | DJGUL00209_ | 52ML | DIGITAL |  | IT20 (DJ20) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00209_BAIS | 045 | DJGUL00209_ | BAIS | DIGITAL |  | IT20 (DJ20) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00209_0EST | 045 | DJGUL00209_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | IT20 (DJ20) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVALIDO | Discrete | Double-Bit |  | Multibit | 2077;2078 | BRK_045DJGUL00109
045DJGUL00209_FLTC | 045 | DJGUL00209_ | FLTC | DIGITAL |  | IT20 (DJ20) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00209_0EXT | 045 | DJGUL00209_ | 0EXT | DIGITAL |  | IT20 (DJ20) | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00209_UCGS | 045 | DJGUL00209_ | UCGS | DIGITAL |  | IT20 (DJ20) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00209_00DF | 045 | DJGUL00209_ | 00DF | DIGITAL |  | IT20 (DJ20) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGUL00209_00LR | 045 | DJGUL00209_ | 00LR | DIGITAL |  | IT20 (DJ20) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO
045DJGUL00209_NMFL | 045 | DJGUL00209_ | NMFL | DIGITAL |  | IT20 (DJ20) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00219_50FA | 045 | DJGUL00219_ | 50FA | DIGITAL |  | DJ21 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00219_50FB | 045 | DJGUL00219_ | 50FB | DIGITAL |  | DJ21 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00219_50NE | 045 | DJGUL00219_ | 50NE | DIGITAL |  | DJ21 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00219_50FV | 045 | DJGUL00219_ | 50FV | DIGITAL |  | DJ21 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00219_51AP | 045 | DJGUL00219_ | 51AP | DIGITAL | N2= ELIPSE | DJ21 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00219_51FA | 045 | DJGUL00219_ | 51FA | DIGITAL |  | DJ21 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00219_51BP | 045 | DJGUL00219_ | 51BP | DIGITAL | N2= ELIPSE | DJ21 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00219_51FB | 045 | DJGUL00219_ | 51FB | DIGITAL |  | DJ21 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00219_51NP | 045 | DJGUL00219_ | 51NP | DIGITAL | N2= ELIPSE | DJ21 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00219_51NE | 045 | DJGUL00219_ | 51NE | DIGITAL |  | DJ21 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00219_51VP | 045 | DJGUL00219_ | 51VP | DIGITAL | N2= ELIPSE | DJ21 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00219_51FV | 045 | DJGUL00219_ | 51FV | DIGITAL |  | DJ21 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00219_51NB | 045 | DJGUL00219_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ21 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00219_NMFL | 045 | DJGUL00219_ | NMFL | DIGITAL |  | DJ21 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_52BF | 045 | DJGUL00219_ | 52BF | DIGITAL | N2= ELIPSE | DJ21 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00219_CBTL | 045 | DJGUL00219_ | CBTL | DIGITAL |  | DJ21 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00219_8612 | 045 | DJGUL00219_ | 8612 | DIGITAL | N2= ELIPSE | DJ21 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00219_LVAB | 045 | DJGUL00219_ | LVAB | DIGITAL |  | DJ21 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_0DPT | 045 | DJGUL00219_ | 0DPT | DIGITAL |  | DJ21 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_52ML | 045 | DJGUL00219_ | 52ML | DIGITAL |  | DJ21 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00219_BAIS | 045 | DJGUL00219_ | BAIS | DIGITAL |  | DJ21 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00219_TADJ | 045 | DJGUL00219_ | TADJ | DIGITAL | N2= ELIPSE | DJ21 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00219_00TM | 045 | DJGUL00219_ | 00TM | DIGITAL | N2= ELIPSE | DJ21 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00219_TFDJ | 045 | DJGUL00219_ | TFDJ | DIGITAL | N2= ELIPSE | DJ21 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00219_FLTC | 045 | DJGUL00219_ | FLTC | DIGITAL |  | DJ21 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00219_O791 | 045 | DJGUL00219_ | O791 | DIGITAL |  | DJ21 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00219_O792 | 045 | DJGUL00219_ | O792 | DIGITAL |  | DJ21 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00219_00FD | 045 | DJGUL00219_ | 00FD | DIGITAL |  | DJ21 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00219_79BP | 045 | DJGUL00219_ | 79BP | DIGITAL |  | DJ21 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00219_OO79 | 045 | DJGUL00219_ | OO79 | COMANDO / DIGITAL |  | DJ21 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00219_CHVS | 045 | DJGUL00219_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ21 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00219_0EXT | 045 | DJGUL00219_ | 0EXT | DIGITAL |  | DJ21 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00219_0EST | 045 | DJGUL00219_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ21 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00219_027G | 045 | DJGUL00219_ | 027G | DIGITAL | N2= ELIPSE | DJ21 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00219_UCGS | 045 | DJGUL00219_ | UCGS | DIGITAL |  | DJ21 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00219_AJM1 | 045 | DJGUL00219_ | AJM1 | DIGITAL |  | DJ21 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00219_AJM2 | 045 | DJGUL00219_ | AJM2 | DIGITAL |  | DJ21 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00219_AJM3 | 045 | DJGUL00219_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ21 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00219_LVVA | 045 | DJGUL00219_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ21 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00219_MREQ | 045 | DJGUL00219_ | MREQ | DIGITAL | N2= ELIPSE | DJ21 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00219_IATA | 045 | DJGUL00219_ | IATA | DIGITAL |  | DJ21 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_IATB | 045 | DJGUL00219_ | IATB | DIGITAL |  | DJ21 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_IATN | 045 | DJGUL00219_ | IATN | DIGITAL |  | DJ21 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_IATV | 045 | DJGUL00219_ | IATV | DIGITAL |  | DJ21 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_55SB | 045 | DJGUL00219_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ21 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00219_0REC | 045 | DJGUL00219_ | 0REC | DIGITAL | N2= ELIPSE | DJ21 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00219_REAQ | 045 | DJGUL00219_ | REAQ | DIGITAL | N2= ELIPSE | DJ21 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00219_551S | 045 | DJGUL00219_ | 551S | DIGITAL |  | DJ21 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_00SS | 045 | DJGUL00219_ | 00SS | DIGITAL |  | DJ21 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_027G | 045 | DJGUL00219_ | 027G | DIGITAL | N2= ELIPSE | DJ21 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00219_00LR | 045 | DJGUL00219_ | 00LR | DIGITAL |  | DJ21 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00219_00DF | 045 | DJGUL00219_ | 00DF | DIGITAL |  | DJ21 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00229_50FA | 045 | DJGUL00229_ | 50FA | DIGITAL |  | DJ22 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00229_50FB | 045 | DJGUL00229_ | 50FB | DIGITAL |  | DJ22 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00229_50NE | 045 | DJGUL00229_ | 50NE | DIGITAL |  | DJ22 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00229_50FV | 045 | DJGUL00229_ | 50FV | DIGITAL |  | DJ22 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00229_51AP | 045 | DJGUL00229_ | 51AP | DIGITAL | N2= ELIPSE | DJ22 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00229_51FA | 045 | DJGUL00229_ | 51FA | DIGITAL |  | DJ22 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00229_51BP | 045 | DJGUL00229_ | 51BP | DIGITAL | N2= ELIPSE | DJ22 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00229_51FB | 045 | DJGUL00229_ | 51FB | DIGITAL |  | DJ22 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00229_51NP | 045 | DJGUL00229_ | 51NP | DIGITAL | N2= ELIPSE | DJ22 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00229_51NE | 045 | DJGUL00229_ | 51NE | DIGITAL |  | DJ22 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00229_51VP | 045 | DJGUL00229_ | 51VP | DIGITAL | N2= ELIPSE | DJ22 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00229_51FV | 045 | DJGUL00229_ | 51FV | DIGITAL |  | DJ22 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00229_51NB | 045 | DJGUL00229_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ22 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00229_NMFL | 045 | DJGUL00229_ | NMFL | DIGITAL |  | DJ22 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_52BF | 045 | DJGUL00229_ | 52BF | DIGITAL | N2= ELIPSE | DJ22 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00229_CBTL | 045 | DJGUL00229_ | CBTL | DIGITAL |  | DJ22 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00229_8612 | 045 | DJGUL00229_ | 8612 | DIGITAL | N2= ELIPSE | DJ22 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00229_LVAB | 045 | DJGUL00229_ | LVAB | DIGITAL |  | DJ22 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_0DPT | 045 | DJGUL00229_ | 0DPT | DIGITAL |  | DJ22 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_52ML | 045 | DJGUL00229_ | 52ML | DIGITAL |  | DJ22 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00229_BAIS | 045 | DJGUL00229_ | BAIS | DIGITAL |  | DJ22 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00229_TADJ | 045 | DJGUL00229_ | TADJ | DIGITAL | N2= ELIPSE | DJ22 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00229_00TM | 045 | DJGUL00229_ | 00TM | DIGITAL | N2= ELIPSE | DJ22 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00229_TFDJ | 045 | DJGUL00229_ | TFDJ | DIGITAL | N2= ELIPSE | DJ22 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00229_FLTC | 045 | DJGUL00229_ | FLTC | DIGITAL |  | DJ22 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00229_O791 | 045 | DJGUL00229_ | O791 | DIGITAL |  | DJ22 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00229_O792 | 045 | DJGUL00229_ | O792 | DIGITAL |  | DJ22 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00229_00FD | 045 | DJGUL00229_ | 00FD | DIGITAL |  | DJ22 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00229_79BP | 045 | DJGUL00229_ | 79BP | DIGITAL |  | DJ22 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00229_OO79 | 045 | DJGUL00229_ | OO79 | COMANDO / DIGITAL |  | DJ22 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00229_CHVS | 045 | DJGUL00229_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ22 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00229_0EXT | 045 | DJGUL00229_ | 0EXT | DIGITAL |  | DJ22 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00229_0EST | 045 | DJGUL00229_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ22 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00229_027G | 045 | DJGUL00229_ | 027G | DIGITAL | N2= ELIPSE | DJ22 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00229_UCGS | 045 | DJGUL00229_ | UCGS | DIGITAL |  | DJ22 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00229_AJM1 | 045 | DJGUL00229_ | AJM1 | DIGITAL |  | DJ22 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00229_AJM2 | 045 | DJGUL00229_ | AJM2 | DIGITAL |  | DJ22 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00229_AJM3 | 045 | DJGUL00229_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ22 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00229_LVVA | 045 | DJGUL00229_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ22 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00229_MREQ | 045 | DJGUL00229_ | MREQ | DIGITAL | N2= ELIPSE | DJ22 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00229_IATA | 045 | DJGUL00229_ | IATA | DIGITAL |  | DJ22 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_IATB | 045 | DJGUL00229_ | IATB | DIGITAL |  | DJ22 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_IATN | 045 | DJGUL00229_ | IATN | DIGITAL |  | DJ22 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_IATV | 045 | DJGUL00229_ | IATV | DIGITAL |  | DJ22 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_55SB | 045 | DJGUL00229_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ22 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00229_0REC | 045 | DJGUL00229_ | 0REC | DIGITAL | N2= ELIPSE | DJ22 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00229_REAQ | 045 | DJGUL00229_ | REAQ | DIGITAL | N2= ELIPSE | DJ22 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00229_551S | 045 | DJGUL00229_ | 551S | DIGITAL |  | DJ22 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_00SS | 045 | DJGUL00229_ | 00SS | DIGITAL |  | DJ22 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_027G | 045 | DJGUL00229_ | 027G | DIGITAL | N2= ELIPSE | DJ22 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00229_00LR | 045 | DJGUL00229_ | 00LR | DIGITAL |  | DJ22 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00229_00DF | 045 | DJGUL00229_ | 00DF | DIGITAL |  | DJ22 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00239_50FA | 045 | DJGUL00239_ | 50FA | DIGITAL |  | DJ23 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00239_50FB | 045 | DJGUL00239_ | 50FB | DIGITAL |  | DJ23 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00239_50NE | 045 | DJGUL00239_ | 50NE | DIGITAL |  | DJ23 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00239_50FV | 045 | DJGUL00239_ | 50FV | DIGITAL |  | DJ23 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00239_51AP | 045 | DJGUL00239_ | 51AP | DIGITAL | N2= ELIPSE | DJ23 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00239_51FA | 045 | DJGUL00239_ | 51FA | DIGITAL |  | DJ23 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00239_51BP | 045 | DJGUL00239_ | 51BP | DIGITAL | N2= ELIPSE | DJ23 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00239_51FB | 045 | DJGUL00239_ | 51FB | DIGITAL |  | DJ23 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00239_51NP | 045 | DJGUL00239_ | 51NP | DIGITAL | N2= ELIPSE | DJ23 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00239_51NE | 045 | DJGUL00239_ | 51NE | DIGITAL |  | DJ23 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00239_51VP | 045 | DJGUL00239_ | 51VP | DIGITAL | N2= ELIPSE | DJ23 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00239_51FV | 045 | DJGUL00239_ | 51FV | DIGITAL |  | DJ23 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00239_51NB | 045 | DJGUL00239_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ23 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00239_NMFL | 045 | DJGUL00239_ | NMFL | DIGITAL |  | DJ23 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_52BF | 045 | DJGUL00239_ | 52BF | DIGITAL | N2= ELIPSE | DJ23 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00239_CBTL | 045 | DJGUL00239_ | CBTL | DIGITAL |  | DJ23 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00239_8612 | 045 | DJGUL00239_ | 8612 | DIGITAL | N2= ELIPSE | DJ23 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00239_LVAB | 045 | DJGUL00239_ | LVAB | DIGITAL |  | DJ23 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_0DPT | 045 | DJGUL00239_ | 0DPT | DIGITAL |  | DJ23 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_52ML | 045 | DJGUL00239_ | 52ML | DIGITAL |  | DJ23 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00239_BAIS | 045 | DJGUL00239_ | BAIS | DIGITAL |  | DJ23 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00239_TADJ | 045 | DJGUL00239_ | TADJ | DIGITAL | N2= ELIPSE | DJ23 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00239_00TM | 045 | DJGUL00239_ | 00TM | DIGITAL | N2= ELIPSE | DJ23 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00239_TFDJ | 045 | DJGUL00239_ | TFDJ | DIGITAL | N2= ELIPSE | DJ23 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00239_FLTC | 045 | DJGUL00239_ | FLTC | DIGITAL |  | DJ23 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00239_O791 | 045 | DJGUL00239_ | O791 | DIGITAL |  | DJ23 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00239_O792 | 045 | DJGUL00239_ | O792 | DIGITAL |  | DJ23 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00239_00FD | 045 | DJGUL00239_ | 00FD | DIGITAL |  | DJ23 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00239_79BP | 045 | DJGUL00239_ | 79BP | DIGITAL |  | DJ23 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00239_OO79 | 045 | DJGUL00239_ | OO79 | COMANDO / DIGITAL |  | DJ23 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00239_CHVS | 045 | DJGUL00239_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ23 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00239_0EXT | 045 | DJGUL00239_ | 0EXT | DIGITAL |  | DJ23 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00239_0EST | 045 | DJGUL00239_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ23 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00239_027G | 045 | DJGUL00239_ | 027G | DIGITAL | N2= ELIPSE | DJ23 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00239_UCGS | 045 | DJGUL00239_ | UCGS | DIGITAL |  | DJ23 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00239_AJM1 | 045 | DJGUL00239_ | AJM1 | DIGITAL |  | DJ23 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00239_AJM2 | 045 | DJGUL00239_ | AJM2 | DIGITAL |  | DJ23 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00239_AJM3 | 045 | DJGUL00239_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ23 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00239_LVVA | 045 | DJGUL00239_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ23 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00239_MREQ | 045 | DJGUL00239_ | MREQ | DIGITAL | N2= ELIPSE | DJ23 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00239_IATA | 045 | DJGUL00239_ | IATA | DIGITAL |  | DJ23 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_IATB | 045 | DJGUL00239_ | IATB | DIGITAL |  | DJ23 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_IATN | 045 | DJGUL00239_ | IATN | DIGITAL |  | DJ23 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_IATV | 045 | DJGUL00239_ | IATV | DIGITAL |  | DJ23 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_55SB | 045 | DJGUL00239_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ23 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00239_0REC | 045 | DJGUL00239_ | 0REC | DIGITAL | N2= ELIPSE | DJ23 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00239_REAQ | 045 | DJGUL00239_ | REAQ | DIGITAL | N2= ELIPSE | DJ23 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00239_551S | 045 | DJGUL00239_ | 551S | DIGITAL |  | DJ23 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_00SS | 045 | DJGUL00239_ | 00SS | DIGITAL |  | DJ23 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_027G | 045 | DJGUL00239_ | 027G | DIGITAL | N2= ELIPSE | DJ23 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00239_00LR | 045 | DJGUL00239_ | 00LR | DIGITAL |  | DJ23 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00239_00DF | 045 | DJGUL00239_ | 00DF | DIGITAL |  | DJ23 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00249_50FA | 045 | DJGUL00249_ | 50FA | DIGITAL |  | DJ24 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00249_50FB | 045 | DJGUL00249_ | 50FB | DIGITAL |  | DJ24 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00249_50NE | 045 | DJGUL00249_ | 50NE | DIGITAL |  | DJ24 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00249_50FV | 045 | DJGUL00249_ | 50FV | DIGITAL |  | DJ24 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00249_51AP | 045 | DJGUL00249_ | 51AP | DIGITAL | N2= ELIPSE | DJ24 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00249_51FA | 045 | DJGUL00249_ | 51FA | DIGITAL |  | DJ24 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00249_51BP | 045 | DJGUL00249_ | 51BP | DIGITAL | N2= ELIPSE | DJ24 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00249_51FB | 045 | DJGUL00249_ | 51FB | DIGITAL |  | DJ24 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00249_51NP | 045 | DJGUL00249_ | 51NP | DIGITAL | N2= ELIPSE | DJ24 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00249_51NE | 045 | DJGUL00249_ | 51NE | DIGITAL |  | DJ24 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00249_51VP | 045 | DJGUL00249_ | 51VP | DIGITAL | N2= ELIPSE | DJ24 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00249_51FV | 045 | DJGUL00249_ | 51FV | DIGITAL |  | DJ24 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00249_51NB | 045 | DJGUL00249_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ24 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00249_NMFL | 045 | DJGUL00249_ | NMFL | DIGITAL |  | DJ24 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_52BF | 045 | DJGUL00249_ | 52BF | DIGITAL | N2= ELIPSE | DJ24 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00249_CBTL | 045 | DJGUL00249_ | CBTL | DIGITAL |  | DJ24 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00249_8612 | 045 | DJGUL00249_ | 8612 | DIGITAL | N2= ELIPSE | DJ24 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00249_LVAB | 045 | DJGUL00249_ | LVAB | DIGITAL |  | DJ24 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_0DPT | 045 | DJGUL00249_ | 0DPT | DIGITAL |  | DJ24 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_52ML | 045 | DJGUL00249_ | 52ML | DIGITAL |  | DJ24 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00249_BAIS | 045 | DJGUL00249_ | BAIS | DIGITAL |  | DJ24 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00249_TADJ | 045 | DJGUL00249_ | TADJ | DIGITAL | N2= ELIPSE | DJ24 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00249_00TM | 045 | DJGUL00249_ | 00TM | DIGITAL | N2= ELIPSE | DJ24 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00249_TFDJ | 045 | DJGUL00249_ | TFDJ | DIGITAL | N2= ELIPSE | DJ24 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00249_FLTC | 045 | DJGUL00249_ | FLTC | DIGITAL |  | DJ24 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00249_O791 | 045 | DJGUL00249_ | O791 | DIGITAL |  | DJ24 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00249_O792 | 045 | DJGUL00249_ | O792 | DIGITAL |  | DJ24 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00249_00FD | 045 | DJGUL00249_ | 00FD | DIGITAL |  | DJ24 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00249_79BP | 045 | DJGUL00249_ | 79BP | DIGITAL |  | DJ24 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00249_OO79 | 045 | DJGUL00249_ | OO79 | COMANDO / DIGITAL |  | DJ24 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00249_CHVS | 045 | DJGUL00249_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ24 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00249_0EXT | 045 | DJGUL00249_ | 0EXT | DIGITAL |  | DJ24 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00249_0EST | 045 | DJGUL00249_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ24 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00249_027G | 045 | DJGUL00249_ | 027G | DIGITAL | N2= ELIPSE | DJ24 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00249_UCGS | 045 | DJGUL00249_ | UCGS | DIGITAL |  | DJ24 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00249_AJM1 | 045 | DJGUL00249_ | AJM1 | DIGITAL |  | DJ24 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00249_AJM2 | 045 | DJGUL00249_ | AJM2 | DIGITAL |  | DJ24 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00249_AJM3 | 045 | DJGUL00249_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ24 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00249_LVVA | 045 | DJGUL00249_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ24 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00249_MREQ | 045 | DJGUL00249_ | MREQ | DIGITAL | N2= ELIPSE | DJ24 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00249_IATA | 045 | DJGUL00249_ | IATA | DIGITAL |  | DJ24 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_IATB | 045 | DJGUL00249_ | IATB | DIGITAL |  | DJ24 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_IATN | 045 | DJGUL00249_ | IATN | DIGITAL |  | DJ24 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_IATV | 045 | DJGUL00249_ | IATV | DIGITAL |  | DJ24 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_55SB | 045 | DJGUL00249_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ24 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00249_0REC | 045 | DJGUL00249_ | 0REC | DIGITAL | N2= ELIPSE | DJ24 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00249_REAQ | 045 | DJGUL00249_ | REAQ | DIGITAL | N2= ELIPSE | DJ24 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00249_551S | 045 | DJGUL00249_ | 551S | DIGITAL |  | DJ24 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_00SS | 045 | DJGUL00249_ | 00SS | DIGITAL |  | DJ24 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_027G | 045 | DJGUL00249_ | 027G | DIGITAL | N2= ELIPSE | DJ24 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00249_00LR | 045 | DJGUL00249_ | 00LR | DIGITAL |  | DJ24 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00249_00DF | 045 | DJGUL00249_ | 00DF | DIGITAL |  | DJ24 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00259_50FA | 045 | DJGUL00259_ | 50FA | DIGITAL |  | DJ25 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00259_50FB | 045 | DJGUL00259_ | 50FB | DIGITAL |  | DJ25 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00259_50NE | 045 | DJGUL00259_ | 50NE | DIGITAL |  | DJ25 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00259_50FV | 045 | DJGUL00259_ | 50FV | DIGITAL |  | DJ25 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00259_51AP | 045 | DJGUL00259_ | 51AP | DIGITAL | N2= ELIPSE | DJ25 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00259_51FA | 045 | DJGUL00259_ | 51FA | DIGITAL |  | DJ25 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00259_51BP | 045 | DJGUL00259_ | 51BP | DIGITAL | N2= ELIPSE | DJ25 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00259_51FB | 045 | DJGUL00259_ | 51FB | DIGITAL |  | DJ25 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00259_51NP | 045 | DJGUL00259_ | 51NP | DIGITAL | N2= ELIPSE | DJ25 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00259_51NE | 045 | DJGUL00259_ | 51NE | DIGITAL |  | DJ25 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00259_51VP | 045 | DJGUL00259_ | 51VP | DIGITAL | N2= ELIPSE | DJ25 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00259_51FV | 045 | DJGUL00259_ | 51FV | DIGITAL |  | DJ25 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00259_51NB | 045 | DJGUL00259_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ25 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00259_NMFL | 045 | DJGUL00259_ | NMFL | DIGITAL |  | DJ25 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_52BF | 045 | DJGUL00259_ | 52BF | DIGITAL | N2= ELIPSE | DJ25 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00259_CBTL | 045 | DJGUL00259_ | CBTL | DIGITAL |  | DJ25 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00259_8612 | 045 | DJGUL00259_ | 8612 | DIGITAL | N2= ELIPSE | DJ25 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00259_LVAB | 045 | DJGUL00259_ | LVAB | DIGITAL |  | DJ25 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_0DPT | 045 | DJGUL00259_ | 0DPT | DIGITAL |  | DJ25 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_52ML | 045 | DJGUL00259_ | 52ML | DIGITAL |  | DJ25 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00259_BAIS | 045 | DJGUL00259_ | BAIS | DIGITAL |  | DJ25 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00259_TADJ | 045 | DJGUL00259_ | TADJ | DIGITAL | N2= ELIPSE | DJ25 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00259_00TM | 045 | DJGUL00259_ | 00TM | DIGITAL | N2= ELIPSE | DJ25 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00259_TFDJ | 045 | DJGUL00259_ | TFDJ | DIGITAL | N2= ELIPSE | DJ25 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00259_FLTC | 045 | DJGUL00259_ | FLTC | DIGITAL |  | DJ25 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00259_O791 | 045 | DJGUL00259_ | O791 | DIGITAL |  | DJ25 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00259_O792 | 045 | DJGUL00259_ | O792 | DIGITAL |  | DJ25 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00259_00FD | 045 | DJGUL00259_ | 00FD | DIGITAL |  | DJ25 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00259_79BP | 045 | DJGUL00259_ | 79BP | DIGITAL |  | DJ25 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00259_OO79 | 045 | DJGUL00259_ | OO79 | COMANDO / DIGITAL |  | DJ25 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00259_CHVS | 045 | DJGUL00259_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ25 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00259_0EXT | 045 | DJGUL00259_ | 0EXT | DIGITAL |  | DJ25 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00259_0EST | 045 | DJGUL00259_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ25 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00259_027G | 045 | DJGUL00259_ | 027G | DIGITAL | N2= ELIPSE | DJ25 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00259_UCGS | 045 | DJGUL00259_ | UCGS | DIGITAL |  | DJ25 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00259_AJM1 | 045 | DJGUL00259_ | AJM1 | DIGITAL |  | DJ25 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00259_AJM2 | 045 | DJGUL00259_ | AJM2 | DIGITAL |  | DJ25 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00259_AJM3 | 045 | DJGUL00259_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ25 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00259_LVVA | 045 | DJGUL00259_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ25 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00259_MREQ | 045 | DJGUL00259_ | MREQ | DIGITAL | N2= ELIPSE | DJ25 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00259_IATA | 045 | DJGUL00259_ | IATA | DIGITAL |  | DJ25 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_IATB | 045 | DJGUL00259_ | IATB | DIGITAL |  | DJ25 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_IATN | 045 | DJGUL00259_ | IATN | DIGITAL |  | DJ25 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_IATV | 045 | DJGUL00259_ | IATV | DIGITAL |  | DJ25 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_55SB | 045 | DJGUL00259_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ25 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00259_0REC | 045 | DJGUL00259_ | 0REC | DIGITAL | N2= ELIPSE | DJ25 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00259_REAQ | 045 | DJGUL00259_ | REAQ | DIGITAL | N2= ELIPSE | DJ25 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00259_551S | 045 | DJGUL00259_ | 551S | DIGITAL |  | DJ25 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_00SS | 045 | DJGUL00259_ | 00SS | DIGITAL |  | DJ25 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_027G | 045 | DJGUL00259_ | 027G | DIGITAL | N2= ELIPSE | DJ25 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00259_00LR | 045 | DJGUL00259_ | 00LR | DIGITAL |  | DJ25 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00259_00DF | 045 | DJGUL00259_ | 00DF | DIGITAL |  | DJ25 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00269_50FA | 045 | DJGUL00269_ | 50FA | DIGITAL |  | DJ26 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00269_50FB | 045 | DJGUL00269_ | 50FB | DIGITAL |  | DJ26 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00269_50NE | 045 | DJGUL00269_ | 50NE | DIGITAL |  | DJ26 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00269_50FV | 045 | DJGUL00269_ | 50FV | DIGITAL |  | DJ26 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00269_51AP | 045 | DJGUL00269_ | 51AP | DIGITAL | N2= ELIPSE | DJ26 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00269_51FA | 045 | DJGUL00269_ | 51FA | DIGITAL |  | DJ26 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00269_51BP | 045 | DJGUL00269_ | 51BP | DIGITAL | N2= ELIPSE | DJ26 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00269_51FB | 045 | DJGUL00269_ | 51FB | DIGITAL |  | DJ26 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00269_51NP | 045 | DJGUL00269_ | 51NP | DIGITAL | N2= ELIPSE | DJ26 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00269_51NE | 045 | DJGUL00269_ | 51NE | DIGITAL |  | DJ26 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00269_51VP | 045 | DJGUL00269_ | 51VP | DIGITAL | N2= ELIPSE | DJ26 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00269_51FV | 045 | DJGUL00269_ | 51FV | DIGITAL |  | DJ26 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00269_51NB | 045 | DJGUL00269_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ26 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00269_NMFL | 045 | DJGUL00269_ | NMFL | DIGITAL |  | DJ26 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_52BF | 045 | DJGUL00269_ | 52BF | DIGITAL | N2= ELIPSE | DJ26 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00269_CBTL | 045 | DJGUL00269_ | CBTL | DIGITAL |  | DJ26 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00269_8612 | 045 | DJGUL00269_ | 8612 | DIGITAL | N2= ELIPSE | DJ26 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00269_LVAB | 045 | DJGUL00269_ | LVAB | DIGITAL |  | DJ26 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_0DPT | 045 | DJGUL00269_ | 0DPT | DIGITAL |  | DJ26 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_52ML | 045 | DJGUL00269_ | 52ML | DIGITAL |  | DJ26 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00269_BAIS | 045 | DJGUL00269_ | BAIS | DIGITAL |  | DJ26 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00269_TADJ | 045 | DJGUL00269_ | TADJ | DIGITAL | N2= ELIPSE | DJ26 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00269_00TM | 045 | DJGUL00269_ | 00TM | DIGITAL | N2= ELIPSE | DJ26 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00269_TFDJ | 045 | DJGUL00269_ | TFDJ | DIGITAL | N2= ELIPSE | DJ26 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00269_FLTC | 045 | DJGUL00269_ | FLTC | DIGITAL |  | DJ26 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00269_O791 | 045 | DJGUL00269_ | O791 | DIGITAL |  | DJ26 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00269_O792 | 045 | DJGUL00269_ | O792 | DIGITAL |  | DJ26 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00269_00FD | 045 | DJGUL00269_ | 00FD | DIGITAL |  | DJ26 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00269_79BP | 045 | DJGUL00269_ | 79BP | DIGITAL |  | DJ26 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00269_OO79 | 045 | DJGUL00269_ | OO79 | COMANDO / DIGITAL |  | DJ26 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00269_CHVS | 045 | DJGUL00269_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ26 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00269_0EXT | 045 | DJGUL00269_ | 0EXT | DIGITAL |  | DJ26 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00269_0EST | 045 | DJGUL00269_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ26 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00269_027G | 045 | DJGUL00269_ | 027G | DIGITAL | N2= ELIPSE | DJ26 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00269_UCGS | 045 | DJGUL00269_ | UCGS | DIGITAL |  | DJ26 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00269_AJM1 | 045 | DJGUL00269_ | AJM1 | DIGITAL |  | DJ26 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00269_AJM2 | 045 | DJGUL00269_ | AJM2 | DIGITAL |  | DJ26 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00269_AJM3 | 045 | DJGUL00269_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ26 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00269_LVVA | 045 | DJGUL00269_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ26 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00269_MREQ | 045 | DJGUL00269_ | MREQ | DIGITAL | N2= ELIPSE | DJ26 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00269_IATA | 045 | DJGUL00269_ | IATA | DIGITAL |  | DJ26 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_IATB | 045 | DJGUL00269_ | IATB | DIGITAL |  | DJ26 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_IATN | 045 | DJGUL00269_ | IATN | DIGITAL |  | DJ26 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_IATV | 045 | DJGUL00269_ | IATV | DIGITAL |  | DJ26 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_55SB | 045 | DJGUL00269_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ26 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00269_0REC | 045 | DJGUL00269_ | 0REC | DIGITAL | N2= ELIPSE | DJ26 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00269_REAQ | 045 | DJGUL00269_ | REAQ | DIGITAL | N2= ELIPSE | DJ26 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00269_551S | 045 | DJGUL00269_ | 551S | DIGITAL |  | DJ26 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_00SS | 045 | DJGUL00269_ | 00SS | DIGITAL |  | DJ26 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_027G | 045 | DJGUL00269_ | 027G | DIGITAL | N2= ELIPSE | DJ26 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00269_00LR | 045 | DJGUL00269_ | 00LR | DIGITAL |  | DJ26 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00269_00DF | 045 | DJGUL00269_ | 00DF | DIGITAL |  | DJ26 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00309_CBTL | 045 | DJGUL00309_ | CBTL | DIGITAL |  | IT30 (DJ30) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00309_FLTC | 045 | DJGUL00309_ | FLTC | DIGITAL |  | IT30 (DJ30) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00309_52ML | 045 | DJGUL00309_ | 52ML | DIGITAL |  | IT30 (DJ30) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00309_BAIS | 045 | DJGUL00309_ | BAIS | DIGITAL |  | IT30 (DJ30) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00309_0EST | 045 | DJGUL00309_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | IT30 (DJ30) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVALIDO | Discrete | Double-Bit |  | Multibit | 2077;2078 | BRK_045DJGUL00109
045DJGUL00309_FLTC | 045 | DJGUL00309_ | FLTC | DIGITAL |  | IT30 (DJ30) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00309_0EXT | 045 | DJGUL00309_ | 0EXT | DIGITAL |  | IT30 (DJ30) | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00309_UCGS | 045 | DJGUL00309_ | UCGS | DIGITAL |  | IT30 (DJ30) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00309_00DF | 045 | DJGUL00309_ | 00DF | DIGITAL |  | IT30 (DJ30) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGUL00309_00LR | 045 | DJGUL00309_ | 00LR | DIGITAL |  | IT30 (DJ30) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO
045DJGUL00309_NMFL | 045 | DJGUL00309_ | NMFL | DIGITAL |  | IT30 (DJ30) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00319_50FA | 045 | DJGUL00319_ | 50FA | DIGITAL |  | DJ31 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00319_50FB | 045 | DJGUL00319_ | 50FB | DIGITAL |  | DJ31 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00319_50NE | 045 | DJGUL00319_ | 50NE | DIGITAL |  | DJ31 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00319_50FV | 045 | DJGUL00319_ | 50FV | DIGITAL |  | DJ31 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00319_51AP | 045 | DJGUL00319_ | 51AP | DIGITAL | N2= ELIPSE | DJ31 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00319_51FA | 045 | DJGUL00319_ | 51FA | DIGITAL |  | DJ31 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00319_51BP | 045 | DJGUL00319_ | 51BP | DIGITAL | N2= ELIPSE | DJ31 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00319_51FB | 045 | DJGUL00319_ | 51FB | DIGITAL |  | DJ31 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00319_51NP | 045 | DJGUL00319_ | 51NP | DIGITAL | N2= ELIPSE | DJ31 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00319_51NE | 045 | DJGUL00319_ | 51NE | DIGITAL |  | DJ31 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00319_51VP | 045 | DJGUL00319_ | 51VP | DIGITAL | N2= ELIPSE | DJ31 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00319_51FV | 045 | DJGUL00319_ | 51FV | DIGITAL |  | DJ31 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00319_51NB | 045 | DJGUL00319_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ31 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00319_NMFL | 045 | DJGUL00319_ | NMFL | DIGITAL |  | DJ31 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_52BF | 045 | DJGUL00319_ | 52BF | DIGITAL | N2= ELIPSE | DJ31 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00319_CBTL | 045 | DJGUL00319_ | CBTL | DIGITAL |  | DJ31 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00319_8612 | 045 | DJGUL00319_ | 8612 | DIGITAL | N2= ELIPSE | DJ31 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00319_LVAB | 045 | DJGUL00319_ | LVAB | DIGITAL |  | DJ31 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_0DPT | 045 | DJGUL00319_ | 0DPT | DIGITAL |  | DJ31 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_52ML | 045 | DJGUL00319_ | 52ML | DIGITAL |  | DJ31 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00319_BAIS | 045 | DJGUL00319_ | BAIS | DIGITAL |  | DJ31 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00319_TADJ | 045 | DJGUL00319_ | TADJ | DIGITAL | N2= ELIPSE | DJ31 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00319_00TM | 045 | DJGUL00319_ | 00TM | DIGITAL | N2= ELIPSE | DJ31 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00319_TFDJ | 045 | DJGUL00319_ | TFDJ | DIGITAL | N2= ELIPSE | DJ31 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00319_FLTC | 045 | DJGUL00319_ | FLTC | DIGITAL |  | DJ31 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00319_O791 | 045 | DJGUL00319_ | O791 | DIGITAL |  | DJ31 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00319_O792 | 045 | DJGUL00319_ | O792 | DIGITAL |  | DJ31 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00319_00FD | 045 | DJGUL00319_ | 00FD | DIGITAL |  | DJ31 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00319_79BP | 045 | DJGUL00319_ | 79BP | DIGITAL |  | DJ31 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00319_OO79 | 045 | DJGUL00319_ | OO79 | COMANDO / DIGITAL |  | DJ31 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00319_CHVS | 045 | DJGUL00319_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ31 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00319_0EXT | 045 | DJGUL00319_ | 0EXT | DIGITAL |  | DJ31 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00319_0EST | 045 | DJGUL00319_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ31 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00319_027G | 045 | DJGUL00319_ | 027G | DIGITAL | N2= ELIPSE | DJ31 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00319_UCGS | 045 | DJGUL00319_ | UCGS | DIGITAL |  | DJ31 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00319_AJM1 | 045 | DJGUL00319_ | AJM1 | DIGITAL |  | DJ31 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00319_AJM2 | 045 | DJGUL00319_ | AJM2 | DIGITAL |  | DJ31 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00319_AJM3 | 045 | DJGUL00319_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ31 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00319_LVVA | 045 | DJGUL00319_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ31 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00319_MREQ | 045 | DJGUL00319_ | MREQ | DIGITAL | N2= ELIPSE | DJ31 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00319_IATA | 045 | DJGUL00319_ | IATA | DIGITAL |  | DJ31 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_IATB | 045 | DJGUL00319_ | IATB | DIGITAL |  | DJ31 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_IATN | 045 | DJGUL00319_ | IATN | DIGITAL |  | DJ31 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_IATV | 045 | DJGUL00319_ | IATV | DIGITAL |  | DJ31 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_55SB | 045 | DJGUL00319_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ31 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00319_0REC | 045 | DJGUL00319_ | 0REC | DIGITAL | N2= ELIPSE | DJ31 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00319_REAQ | 045 | DJGUL00319_ | REAQ | DIGITAL | N2= ELIPSE | DJ31 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00319_551S | 045 | DJGUL00319_ | 551S | DIGITAL |  | DJ31 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_00SS | 045 | DJGUL00319_ | 00SS | DIGITAL |  | DJ31 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_027G | 045 | DJGUL00319_ | 027G | DIGITAL | N2= ELIPSE | DJ31 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00319_00LR | 045 | DJGUL00319_ | 00LR | DIGITAL |  | DJ31 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00319_00DF | 045 | DJGUL00319_ | 00DF | DIGITAL |  | DJ31 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00329_50FA | 045 | DJGUL00329_ | 50FA | DIGITAL |  | DJ32 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00329_50FB | 045 | DJGUL00329_ | 50FB | DIGITAL |  | DJ32 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00329_50NE | 045 | DJGUL00329_ | 50NE | DIGITAL |  | DJ32 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00329_50FV | 045 | DJGUL00329_ | 50FV | DIGITAL |  | DJ32 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00329_51AP | 045 | DJGUL00329_ | 51AP | DIGITAL | N2= ELIPSE | DJ32 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00329_51FA | 045 | DJGUL00329_ | 51FA | DIGITAL |  | DJ32 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00329_51BP | 045 | DJGUL00329_ | 51BP | DIGITAL | N2= ELIPSE | DJ32 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00329_51FB | 045 | DJGUL00329_ | 51FB | DIGITAL |  | DJ32 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00329_51NP | 045 | DJGUL00329_ | 51NP | DIGITAL | N2= ELIPSE | DJ32 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00329_51NE | 045 | DJGUL00329_ | 51NE | DIGITAL |  | DJ32 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00329_51VP | 045 | DJGUL00329_ | 51VP | DIGITAL | N2= ELIPSE | DJ32 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00329_51FV | 045 | DJGUL00329_ | 51FV | DIGITAL |  | DJ32 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00329_51NB | 045 | DJGUL00329_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ32 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00329_NMFL | 045 | DJGUL00329_ | NMFL | DIGITAL |  | DJ32 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_52BF | 045 | DJGUL00329_ | 52BF | DIGITAL | N2= ELIPSE | DJ32 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00329_CBTL | 045 | DJGUL00329_ | CBTL | DIGITAL |  | DJ32 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00329_8612 | 045 | DJGUL00329_ | 8612 | DIGITAL | N2= ELIPSE | DJ32 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00329_LVAB | 045 | DJGUL00329_ | LVAB | DIGITAL |  | DJ32 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_0DPT | 045 | DJGUL00329_ | 0DPT | DIGITAL |  | DJ32 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_52ML | 045 | DJGUL00329_ | 52ML | DIGITAL |  | DJ32 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00329_BAIS | 045 | DJGUL00329_ | BAIS | DIGITAL |  | DJ32 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00329_TADJ | 045 | DJGUL00329_ | TADJ | DIGITAL | N2= ELIPSE | DJ32 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00329_00TM | 045 | DJGUL00329_ | 00TM | DIGITAL | N2= ELIPSE | DJ32 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00329_TFDJ | 045 | DJGUL00329_ | TFDJ | DIGITAL | N2= ELIPSE | DJ32 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00329_FLTC | 045 | DJGUL00329_ | FLTC | DIGITAL |  | DJ32 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00329_O791 | 045 | DJGUL00329_ | O791 | DIGITAL |  | DJ32 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00329_O792 | 045 | DJGUL00329_ | O792 | DIGITAL |  | DJ32 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00329_00FD | 045 | DJGUL00329_ | 00FD | DIGITAL |  | DJ32 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00329_79BP | 045 | DJGUL00329_ | 79BP | DIGITAL |  | DJ32 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00329_OO79 | 045 | DJGUL00329_ | OO79 | COMANDO / DIGITAL |  | DJ32 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00329_CHVS | 045 | DJGUL00329_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ32 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00329_0EXT | 045 | DJGUL00329_ | 0EXT | DIGITAL |  | DJ32 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00329_0EST | 045 | DJGUL00329_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ32 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00329_027G | 045 | DJGUL00329_ | 027G | DIGITAL | N2= ELIPSE | DJ32 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00329_UCGS | 045 | DJGUL00329_ | UCGS | DIGITAL |  | DJ32 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00329_AJM1 | 045 | DJGUL00329_ | AJM1 | DIGITAL |  | DJ32 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00329_AJM2 | 045 | DJGUL00329_ | AJM2 | DIGITAL |  | DJ32 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00329_AJM3 | 045 | DJGUL00329_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ32 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00329_LVVA | 045 | DJGUL00329_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ32 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00329_MREQ | 045 | DJGUL00329_ | MREQ | DIGITAL | N2= ELIPSE | DJ32 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00329_IATA | 045 | DJGUL00329_ | IATA | DIGITAL |  | DJ32 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_IATB | 045 | DJGUL00329_ | IATB | DIGITAL |  | DJ32 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_IATN | 045 | DJGUL00329_ | IATN | DIGITAL |  | DJ32 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_IATV | 045 | DJGUL00329_ | IATV | DIGITAL |  | DJ32 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_55SB | 045 | DJGUL00329_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ32 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00329_0REC | 045 | DJGUL00329_ | 0REC | DIGITAL | N2= ELIPSE | DJ32 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00329_REAQ | 045 | DJGUL00329_ | REAQ | DIGITAL | N2= ELIPSE | DJ32 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00329_551S | 045 | DJGUL00329_ | 551S | DIGITAL |  | DJ32 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_00SS | 045 | DJGUL00329_ | 00SS | DIGITAL |  | DJ32 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_027G | 045 | DJGUL00329_ | 027G | DIGITAL | N2= ELIPSE | DJ32 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00329_00LR | 045 | DJGUL00329_ | 00LR | DIGITAL |  | DJ32 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00329_00DF | 045 | DJGUL00329_ | 00DF | DIGITAL |  | DJ32 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00339_50FA | 045 | DJGUL00339_ | 50FA | DIGITAL |  | DJ33 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00339_50FB | 045 | DJGUL00339_ | 50FB | DIGITAL |  | DJ33 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00339_50NE | 045 | DJGUL00339_ | 50NE | DIGITAL |  | DJ33 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00339_50FV | 045 | DJGUL00339_ | 50FV | DIGITAL |  | DJ33 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00339_51AP | 045 | DJGUL00339_ | 51AP | DIGITAL | N2= ELIPSE | DJ33 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00339_51FA | 045 | DJGUL00339_ | 51FA | DIGITAL |  | DJ33 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00339_51BP | 045 | DJGUL00339_ | 51BP | DIGITAL | N2= ELIPSE | DJ33 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00339_51FB | 045 | DJGUL00339_ | 51FB | DIGITAL |  | DJ33 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00339_51NP | 045 | DJGUL00339_ | 51NP | DIGITAL | N2= ELIPSE | DJ33 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00339_51NE | 045 | DJGUL00339_ | 51NE | DIGITAL |  | DJ33 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00339_51VP | 045 | DJGUL00339_ | 51VP | DIGITAL | N2= ELIPSE | DJ33 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00339_51FV | 045 | DJGUL00339_ | 51FV | DIGITAL |  | DJ33 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00339_51NB | 045 | DJGUL00339_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ33 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00339_NMFL | 045 | DJGUL00339_ | NMFL | DIGITAL |  | DJ33 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_52BF | 045 | DJGUL00339_ | 52BF | DIGITAL | N2= ELIPSE | DJ33 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00339_CBTL | 045 | DJGUL00339_ | CBTL | DIGITAL |  | DJ33 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00339_8612 | 045 | DJGUL00339_ | 8612 | DIGITAL | N2= ELIPSE | DJ33 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00339_LVAB | 045 | DJGUL00339_ | LVAB | DIGITAL |  | DJ33 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_0DPT | 045 | DJGUL00339_ | 0DPT | DIGITAL |  | DJ33 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_52ML | 045 | DJGUL00339_ | 52ML | DIGITAL |  | DJ33 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00339_BAIS | 045 | DJGUL00339_ | BAIS | DIGITAL |  | DJ33 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00339_TADJ | 045 | DJGUL00339_ | TADJ | DIGITAL | N2= ELIPSE | DJ33 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00339_00TM | 045 | DJGUL00339_ | 00TM | DIGITAL | N2= ELIPSE | DJ33 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00339_TFDJ | 045 | DJGUL00339_ | TFDJ | DIGITAL | N2= ELIPSE | DJ33 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00339_FLTC | 045 | DJGUL00339_ | FLTC | DIGITAL |  | DJ33 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00339_O791 | 045 | DJGUL00339_ | O791 | DIGITAL |  | DJ33 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00339_O792 | 045 | DJGUL00339_ | O792 | DIGITAL |  | DJ33 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00339_00FD | 045 | DJGUL00339_ | 00FD | DIGITAL |  | DJ33 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00339_79BP | 045 | DJGUL00339_ | 79BP | DIGITAL |  | DJ33 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00339_OO79 | 045 | DJGUL00339_ | OO79 | COMANDO / DIGITAL |  | DJ33 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00339_CHVS | 045 | DJGUL00339_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ33 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00339_0EXT | 045 | DJGUL00339_ | 0EXT | DIGITAL |  | DJ33 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00339_0EST | 045 | DJGUL00339_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ33 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00339_027G | 045 | DJGUL00339_ | 027G | DIGITAL | N2= ELIPSE | DJ33 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00339_UCGS | 045 | DJGUL00339_ | UCGS | DIGITAL |  | DJ33 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00339_AJM1 | 045 | DJGUL00339_ | AJM1 | DIGITAL |  | DJ33 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00339_AJM2 | 045 | DJGUL00339_ | AJM2 | DIGITAL |  | DJ33 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00339_AJM3 | 045 | DJGUL00339_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ33 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00339_LVVA | 045 | DJGUL00339_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ33 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00339_MREQ | 045 | DJGUL00339_ | MREQ | DIGITAL | N2= ELIPSE | DJ33 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00339_IATA | 045 | DJGUL00339_ | IATA | DIGITAL |  | DJ33 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_IATB | 045 | DJGUL00339_ | IATB | DIGITAL |  | DJ33 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_IATN | 045 | DJGUL00339_ | IATN | DIGITAL |  | DJ33 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_IATV | 045 | DJGUL00339_ | IATV | DIGITAL |  | DJ33 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_55SB | 045 | DJGUL00339_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ33 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00339_0REC | 045 | DJGUL00339_ | 0REC | DIGITAL | N2= ELIPSE | DJ33 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00339_REAQ | 045 | DJGUL00339_ | REAQ | DIGITAL | N2= ELIPSE | DJ33 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00339_551S | 045 | DJGUL00339_ | 551S | DIGITAL |  | DJ33 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_00SS | 045 | DJGUL00339_ | 00SS | DIGITAL |  | DJ33 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_027G | 045 | DJGUL00339_ | 027G | DIGITAL | N2= ELIPSE | DJ33 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00339_00LR | 045 | DJGUL00339_ | 00LR | DIGITAL |  | DJ33 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00339_00DF | 045 | DJGUL00339_ | 00DF | DIGITAL |  | DJ33 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00349_50FA | 045 | DJGUL00349_ | 50FA | DIGITAL |  | DJ34 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00349_50FB | 045 | DJGUL00349_ | 50FB | DIGITAL |  | DJ34 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00349_50NE | 045 | DJGUL00349_ | 50NE | DIGITAL |  | DJ34 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00349_50FV | 045 | DJGUL00349_ | 50FV | DIGITAL |  | DJ34 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00349_51AP | 045 | DJGUL00349_ | 51AP | DIGITAL | N2= ELIPSE | DJ34 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00349_51FA | 045 | DJGUL00349_ | 51FA | DIGITAL |  | DJ34 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00349_51BP | 045 | DJGUL00349_ | 51BP | DIGITAL | N2= ELIPSE | DJ34 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00349_51FB | 045 | DJGUL00349_ | 51FB | DIGITAL |  | DJ34 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00349_51NP | 045 | DJGUL00349_ | 51NP | DIGITAL | N2= ELIPSE | DJ34 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00349_51NE | 045 | DJGUL00349_ | 51NE | DIGITAL |  | DJ34 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00349_51VP | 045 | DJGUL00349_ | 51VP | DIGITAL | N2= ELIPSE | DJ34 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00349_51FV | 045 | DJGUL00349_ | 51FV | DIGITAL |  | DJ34 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00349_51NB | 045 | DJGUL00349_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ34 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00349_NMFL | 045 | DJGUL00349_ | NMFL | DIGITAL |  | DJ34 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_52BF | 045 | DJGUL00349_ | 52BF | DIGITAL | N2= ELIPSE | DJ34 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00349_CBTL | 045 | DJGUL00349_ | CBTL | DIGITAL |  | DJ34 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00349_8612 | 045 | DJGUL00349_ | 8612 | DIGITAL | N2= ELIPSE | DJ34 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00349_LVAB | 045 | DJGUL00349_ | LVAB | DIGITAL |  | DJ34 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_0DPT | 045 | DJGUL00349_ | 0DPT | DIGITAL |  | DJ34 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_52ML | 045 | DJGUL00349_ | 52ML | DIGITAL |  | DJ34 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00349_BAIS | 045 | DJGUL00349_ | BAIS | DIGITAL |  | DJ34 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00349_TADJ | 045 | DJGUL00349_ | TADJ | DIGITAL | N2= ELIPSE | DJ34 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00349_00TM | 045 | DJGUL00349_ | 00TM | DIGITAL | N2= ELIPSE | DJ34 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00349_TFDJ | 045 | DJGUL00349_ | TFDJ | DIGITAL | N2= ELIPSE | DJ34 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00349_FLTC | 045 | DJGUL00349_ | FLTC | DIGITAL |  | DJ34 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00349_O791 | 045 | DJGUL00349_ | O791 | DIGITAL |  | DJ34 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00349_O792 | 045 | DJGUL00349_ | O792 | DIGITAL |  | DJ34 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00349_00FD | 045 | DJGUL00349_ | 00FD | DIGITAL |  | DJ34 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00349_79BP | 045 | DJGUL00349_ | 79BP | DIGITAL |  | DJ34 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00349_OO79 | 045 | DJGUL00349_ | OO79 | COMANDO / DIGITAL |  | DJ34 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00349_CHVS | 045 | DJGUL00349_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ34 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00349_0EXT | 045 | DJGUL00349_ | 0EXT | DIGITAL |  | DJ34 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00349_0EST | 045 | DJGUL00349_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ34 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00349_027G | 045 | DJGUL00349_ | 027G | DIGITAL | N2= ELIPSE | DJ34 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00349_UCGS | 045 | DJGUL00349_ | UCGS | DIGITAL |  | DJ34 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00349_AJM1 | 045 | DJGUL00349_ | AJM1 | DIGITAL |  | DJ34 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00349_AJM2 | 045 | DJGUL00349_ | AJM2 | DIGITAL |  | DJ34 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00349_AJM3 | 045 | DJGUL00349_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ34 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00349_LVVA | 045 | DJGUL00349_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ34 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00349_MREQ | 045 | DJGUL00349_ | MREQ | DIGITAL | N2= ELIPSE | DJ34 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00349_IATA | 045 | DJGUL00349_ | IATA | DIGITAL |  | DJ34 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_IATB | 045 | DJGUL00349_ | IATB | DIGITAL |  | DJ34 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_IATN | 045 | DJGUL00349_ | IATN | DIGITAL |  | DJ34 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_IATV | 045 | DJGUL00349_ | IATV | DIGITAL |  | DJ34 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_55SB | 045 | DJGUL00349_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ34 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00349_0REC | 045 | DJGUL00349_ | 0REC | DIGITAL | N2= ELIPSE | DJ34 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00349_REAQ | 045 | DJGUL00349_ | REAQ | DIGITAL | N2= ELIPSE | DJ34 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00349_551S | 045 | DJGUL00349_ | 551S | DIGITAL |  | DJ34 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_00SS | 045 | DJGUL00349_ | 00SS | DIGITAL |  | DJ34 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_027G | 045 | DJGUL00349_ | 027G | DIGITAL | N2= ELIPSE | DJ34 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00349_00LR | 045 | DJGUL00349_ | 00LR | DIGITAL |  | DJ34 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00349_00DF | 045 | DJGUL00349_ | 00DF | DIGITAL |  | DJ34 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00359_50FA | 045 | DJGUL00359_ | 50FA | DIGITAL |  | DJ35 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00359_50FB | 045 | DJGUL00359_ | 50FB | DIGITAL |  | DJ35 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00359_50NE | 045 | DJGUL00359_ | 50NE | DIGITAL |  | DJ35 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00359_50FV | 045 | DJGUL00359_ | 50FV | DIGITAL |  | DJ35 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00359_51AP | 045 | DJGUL00359_ | 51AP | DIGITAL | N2= ELIPSE | DJ35 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00359_51FA | 045 | DJGUL00359_ | 51FA | DIGITAL |  | DJ35 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00359_51BP | 045 | DJGUL00359_ | 51BP | DIGITAL | N2= ELIPSE | DJ35 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00359_51FB | 045 | DJGUL00359_ | 51FB | DIGITAL |  | DJ35 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00359_51NP | 045 | DJGUL00359_ | 51NP | DIGITAL | N2= ELIPSE | DJ35 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00359_51NE | 045 | DJGUL00359_ | 51NE | DIGITAL |  | DJ35 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00359_51VP | 045 | DJGUL00359_ | 51VP | DIGITAL | N2= ELIPSE | DJ35 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00359_51FV | 045 | DJGUL00359_ | 51FV | DIGITAL |  | DJ35 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00359_51NB | 045 | DJGUL00359_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ35 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00359_NMFL | 045 | DJGUL00359_ | NMFL | DIGITAL |  | DJ35 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_52BF | 045 | DJGUL00359_ | 52BF | DIGITAL | N2= ELIPSE | DJ35 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00359_CBTL | 045 | DJGUL00359_ | CBTL | DIGITAL |  | DJ35 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00359_8612 | 045 | DJGUL00359_ | 8612 | DIGITAL | N2= ELIPSE | DJ35 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00359_LVAB | 045 | DJGUL00359_ | LVAB | DIGITAL |  | DJ35 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_0DPT | 045 | DJGUL00359_ | 0DPT | DIGITAL |  | DJ35 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_52ML | 045 | DJGUL00359_ | 52ML | DIGITAL |  | DJ35 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00359_BAIS | 045 | DJGUL00359_ | BAIS | DIGITAL |  | DJ35 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00359_TADJ | 045 | DJGUL00359_ | TADJ | DIGITAL | N2= ELIPSE | DJ35 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00359_00TM | 045 | DJGUL00359_ | 00TM | DIGITAL | N2= ELIPSE | DJ35 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00359_TFDJ | 045 | DJGUL00359_ | TFDJ | DIGITAL | N2= ELIPSE | DJ35 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00359_FLTC | 045 | DJGUL00359_ | FLTC | DIGITAL |  | DJ35 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00359_O791 | 045 | DJGUL00359_ | O791 | DIGITAL |  | DJ35 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00359_O792 | 045 | DJGUL00359_ | O792 | DIGITAL |  | DJ35 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00359_00FD | 045 | DJGUL00359_ | 00FD | DIGITAL |  | DJ35 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00359_79BP | 045 | DJGUL00359_ | 79BP | DIGITAL |  | DJ35 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00359_OO79 | 045 | DJGUL00359_ | OO79 | COMANDO / DIGITAL |  | DJ35 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00359_CHVS | 045 | DJGUL00359_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ35 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00359_0EXT | 045 | DJGUL00359_ | 0EXT | DIGITAL |  | DJ35 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00359_0EST | 045 | DJGUL00359_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ35 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00359_027G | 045 | DJGUL00359_ | 027G | DIGITAL | N2= ELIPSE | DJ35 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00359_UCGS | 045 | DJGUL00359_ | UCGS | DIGITAL |  | DJ35 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00359_AJM1 | 045 | DJGUL00359_ | AJM1 | DIGITAL |  | DJ35 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00359_AJM2 | 045 | DJGUL00359_ | AJM2 | DIGITAL |  | DJ35 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00359_AJM3 | 045 | DJGUL00359_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ35 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00359_LVVA | 045 | DJGUL00359_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ35 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00359_MREQ | 045 | DJGUL00359_ | MREQ | DIGITAL | N2= ELIPSE | DJ35 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00359_IATA | 045 | DJGUL00359_ | IATA | DIGITAL |  | DJ35 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_IATB | 045 | DJGUL00359_ | IATB | DIGITAL |  | DJ35 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_IATN | 045 | DJGUL00359_ | IATN | DIGITAL |  | DJ35 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_IATV | 045 | DJGUL00359_ | IATV | DIGITAL |  | DJ35 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_55SB | 045 | DJGUL00359_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ35 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00359_0REC | 045 | DJGUL00359_ | 0REC | DIGITAL | N2= ELIPSE | DJ35 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00359_REAQ | 045 | DJGUL00359_ | REAQ | DIGITAL | N2= ELIPSE | DJ35 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00359_551S | 045 | DJGUL00359_ | 551S | DIGITAL |  | DJ35 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_00SS | 045 | DJGUL00359_ | 00SS | DIGITAL |  | DJ35 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_027G | 045 | DJGUL00359_ | 027G | DIGITAL | N2= ELIPSE | DJ35 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00359_00LR | 045 | DJGUL00359_ | 00LR | DIGITAL |  | DJ35 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00359_00DF | 045 | DJGUL00359_ | 00DF | DIGITAL |  | DJ35 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00369_50FA | 045 | DJGUL00369_ | 50FA | DIGITAL |  | DJ36 | 50 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 382 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00369_50FB | 045 | DJGUL00369_ | 50FB | DIGITAL |  | DJ36 | 50 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 383 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00369_50NE | 045 | DJGUL00369_ | 50NE | DIGITAL |  | DJ36 | 50 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 385 |  |  | BRK_045DJGUL00139_50N_RS
045DJGUL00369_50FV | 045 | DJGUL00369_ | 50FV | DIGITAL |  | DJ36 | 50 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 384 |  |  | BRK_045DJGUL00139_50_RS
045DJGUL00369_51AP | 045 | DJGUL00369_ | 51AP | DIGITAL | N2= ELIPSE | DJ36 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00369_51FA | 045 | DJGUL00369_ | 51FA | DIGITAL |  | DJ36 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 386 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00369_51BP | 045 | DJGUL00369_ | 51BP | DIGITAL | N2= ELIPSE | DJ36 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00369_51FB | 045 | DJGUL00369_ | 51FB | DIGITAL |  | DJ36 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 387 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00369_51NP | 045 | DJGUL00369_ | 51NP | DIGITAL | N2= ELIPSE | DJ36 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00369_51NE | 045 | DJGUL00369_ | 51NE | DIGITAL |  | DJ36 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 389 |  |  | BRK_045DJGUL00139_51N_RS
045DJGUL00369_51VP | 045 | DJGUL00369_ | 51VP | DIGITAL | N2= ELIPSE | DJ36 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045DJGUL00369_51FV | 045 | DJGUL00369_ | 51FV | DIGITAL |  | DJ36 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 388 |  |  | BRK_045DJGUL00139_51_RS
045DJGUL00369_51NB | 045 | DJGUL00369_ | 51NB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ36 | 51 PROTECAO NE | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO
045DJGUL00369_NMFL | 045 | DJGUL00369_ | NMFL | DIGITAL |  | DJ36 | 52 BF ABERT PROT DISJ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_52BF | 045 | DJGUL00369_ | 52BF | DIGITAL | N2= ELIPSE | DJ36 | 52 BF FALHA DE DISJUNTOR | ATIVADO;DESATIVADO;; | 0;1;2;3 | ATIVADO | DESATIVADO
045DJGUL00369_CBTL | 045 | DJGUL00369_ | CBTL | DIGITAL |  | DJ36 | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;3;2 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 398 |  |  | BRK_045DJGUL00139 | 52 CH BLOQ TELECOMANDO INVERTIDO
045DJGUL00369_8612 | 045 | DJGUL00369_ | 8612 | DIGITAL | N2= ELIPSE | DJ36 | 52 DISJ DESCONEXAO GD | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00369_LVAB | 045 | DJGUL00369_ | LVAB | DIGITAL |  | DJ36 | 52 DISJ DESLIG PROT LINHA VIVA | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_0DPT | 045 | DJGUL00369_ | 0DPT | DIGITAL |  | DJ36 | 52 DISJ DESLIG PROTEÇÃO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_52ML | 045 | DJGUL00369_ | 52ML | DIGITAL |  | DJ36 | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;; | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit | 401 |  |  | BRK_045DJGUL00139
045DJGUL00369_BAIS | 045 | DJGUL00369_ | BAIS | DIGITAL |  | DJ36 | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit | 392 |  |  | BRK_045DJGUL00139
045DJGUL00369_TADJ | 045 | DJGUL00369_ | TADJ | DIGITAL | N2= ELIPSE | DJ36 | 52 TEMPO ABERTURA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00369_00TM | 045 | DJGUL00369_ | 00TM | DIGITAL | N2= ELIPSE | DJ36 | 52 TEMPO CARREGAR MOLA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00369_TFDJ | 045 | DJGUL00369_ | TFDJ | DIGITAL | N2= ELIPSE | DJ36 | 52 TEMPO FECHAMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  |  |  | N2
045DJGUL00369_FLTC | 045 | DJGUL00369_ | FLTC | DIGITAL |  | DJ36 | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 391 |  |  | BRK_045DJGUL00139
045DJGUL00369_O791 | 045 | DJGUL00369_ | O791 | DIGITAL |  | DJ36 | 79 1º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 395 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00369_O792 | 045 | DJGUL00369_ | O792 | DIGITAL |  | DJ36 | 79 2º RELIG AUTOMATICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 396 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00369_00FD | 045 | DJGUL00369_ | 00FD | DIGITAL |  | DJ36 | 79 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 393 |  |  | BRK_045DJGUL00139_Multifuncional_PE
045DJGUL00369_79BP | 045 | DJGUL00369_ | 79BP | DIGITAL |  | DJ36 | 79 RELIG AUTOMATICO | NORMAL;AUTOBLOQUEADO;; | 0;1;2;3 | NORMAL | AUTOBLOQUEADO |  |  | Discrete | Single-Bit | 397 |  |  | BRK_045DJGUL00139
045DJGUL00369_OO79 | 045 | DJGUL00369_ | OO79 | COMANDO / DIGITAL |  | DJ36 | 79 RELIG AUTOMATICO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 394 | Multibit | 2124;2123 | BRK_045DJGUL00139 | 79 RELIG AUTOMATICO INVERTIDO
045DJGUL00369_CHVS | 045 | DJGUL00369_ | CHVS | COMANDO / DIGITAL | N2= ELIPSE | DJ36 | CHK TENS TP SAIDA | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  |  |  | N2
045DJGUL00369_0EXT | 045 | DJGUL00369_ | 0EXT | DIGITAL |  | DJ36 | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00369_0EST | 045 | DJGUL00369_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | DJ36 | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | TRASIÇÃO | INVALIDO | Discrete | Single-Bit | 390 | Multibit | 2121;2122 | BRK_045DJGUL00139
045DJGUL00369_027G | 045 | DJGUL00369_ | 027G | DIGITAL | N2= ELIPSE | DJ36 | DISJUNTOR TP SAIDA | ARMADO;DESARMADO;; | 0;1;2;3 | ARMADO | DESARMADO |  |  |  |  | N2
045DJGUL00369_UCGS | 045 | DJGUL00369_ | UCGS | DIGITAL |  | DJ36 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00369_AJM1 | 045 | DJGUL00369_ | AJM1 | DIGITAL |  | DJ36 | GRUPO DE AJUSTE 1 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00369_AJM2 | 045 | DJGUL00369_ | AJM2 | DIGITAL |  | DJ36 | GRUPO DE AJUSTE 2 | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00369_AJM3 | 045 | DJGUL00369_ | AJM3 | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ36 | GRUPO DE AJUSTE EM MANOBRA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00369_LVVA | 045 | DJGUL00369_ | LVVA | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ36 | LINHA VIVA | DESATIVADO;ATIVADO;; | 0;1;2;3 | DESATIVADO | ATIVADO
045DJGUL00369_MREQ | 045 | DJGUL00369_ | MREQ | DIGITAL | N2= ELIPSE | DJ36 | MANUTENÇÃO REQUERIDA | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045DJGUL00369_IATA | 045 | DJGUL00369_ | IATA | DIGITAL |  | DJ36 | PROT. ALTA CORRENTE AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_IATB | 045 | DJGUL00369_ | IATB | DIGITAL |  | DJ36 | PROT. ALTA CORRENTE BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_IATN | 045 | DJGUL00369_ | IATN | DIGITAL |  | DJ36 | PROT. ALTA CORRENTE NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_IATV | 045 | DJGUL00369_ | IATV | DIGITAL |  | DJ36 | PROT. ALTA CORRENTE VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_55SB | 045 | DJGUL00369_ | 55SB | COMANDO / DIGITAL | OK - INSERIDO - DIGITAL E COMANDO | DJ36 | PROTECAO SEF | BLOQUEADA;ATIVADA;; | 0;1;2;3 | BLOQUEADA | ATIVADA
045DJGUL00369_0REC | 045 | DJGUL00369_ | 0REC | DIGITAL | N2= ELIPSE | DJ36 | RECOMPOSICAO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  |  |  | N2
045DJGUL00369_REAQ | 045 | DJGUL00369_ | REAQ | DIGITAL | N2= ELIPSE | DJ36 | RESISTENCIA DE AQUECIMENTO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045DJGUL00369_551S | 045 | DJGUL00369_ | 551S | DIGITAL |  | DJ36 | SEF | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_00SS | 045 | DJGUL00369_ | 00SS | DIGITAL |  | DJ36 | SKIP SHOT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_027G | 045 | DJGUL00369_ | 027G | DIGITAL | N2= ELIPSE | DJ36 | TENS TP SAIDA | AUSENTE;PRESENTE;; | 0;1;2;3 | AUSENTE | PRESENTE |  |  |  |  | N2
045DJGUL00369_00LR | 045 | DJGUL00369_ | 00LR | DIGITAL |  | DJ36 | UCP-CTRL/PROT/AQUIS. | REMOTO;LOCAL;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 399 |  |  | BRK_045DJGUL00139
045DJGUL00369_00DF | 045 | DJGUL00369_ | 00DF | DIGITAL |  | DJ36 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 400 |  |  | BRK_045DJGUL00139
045DJGUL00409_CBTL | 045 | DJGUL00409_ | CBTL | DIGITAL |  | IT40 (DJ40) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00409_FLTC | 045 | DJGUL00409_ | FLTC | DIGITAL |  | IT40 (DJ40) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00409_52ML | 045 | DJGUL00409_ | 52ML | DIGITAL |  | IT40 (DJ40) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00409_BAIS | 045 | DJGUL00409_ | BAIS | DIGITAL |  | IT40 (DJ40) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00409_0EST | 045 | DJGUL00409_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | IT40 (DJ40) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVALIDO | Discrete | Double-Bit |  | Multibit | 2077;2078 | BRK_045DJGUL00109
045DJGUL00409_FLTC | 045 | DJGUL00409_ | FLTC | DIGITAL |  | IT40 (DJ40) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00409_0EXT | 045 | DJGUL00409_ | 0EXT | DIGITAL |  | IT40 (DJ40) | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00409_UCGS | 045 | DJGUL00409_ | UCGS | DIGITAL |  | IT40 (DJ40) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00409_00DF | 045 | DJGUL00409_ | 00DF | DIGITAL |  | IT40 (DJ40) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGUL00409_00LR | 045 | DJGUL00409_ | 00LR | DIGITAL |  | IT40 (DJ40) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO
045DJGUL00409_NMFL | 045 | DJGUL00409_ | NMFL | DIGITAL |  | IT40 (DJ40) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00509_CBTL | 045 | DJGUL00509_ | CBTL | DIGITAL |  | IT50 (DJ50) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00509_FLTC | 045 | DJGUL00509_ | FLTC | DIGITAL |  | IT50 (DJ50) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00509_52ML | 045 | DJGUL00509_ | 52ML | DIGITAL |  | IT50 (DJ50) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00509_BAIS | 045 | DJGUL00509_ | BAIS | DIGITAL |  | IT50 (DJ50) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00509_0EST | 045 | DJGUL00509_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | IT50 (DJ50) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVALIDO | Discrete | Double-Bit |  | Multibit | 2077;2078 | BRK_045DJGUL00109
045DJGUL00509_FLTC | 045 | DJGUL00509_ | FLTC | DIGITAL |  | IT50 (DJ50) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00509_0EXT | 045 | DJGUL00509_ | 0EXT | DIGITAL |  | IT50 (DJ50) | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00509_UCGS | 045 | DJGUL00509_ | UCGS | DIGITAL |  | IT50 (DJ50) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00509_00DF | 045 | DJGUL00509_ | 00DF | DIGITAL |  | IT50 (DJ50) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGUL00509_00LR | 045 | DJGUL00509_ | 00LR | DIGITAL |  | IT50 (DJ50) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO
045DJGUL00509_NMFL | 045 | DJGUL00509_ | NMFL | DIGITAL |  | IT50 (DJ50) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00609_CBTL | 045 | DJGUL00609_ | CBTL | DIGITAL |  | IT60 (DJ60) | 52 CH BLOQ TELECOMANDO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00609_FLTC | 045 | DJGUL00609_ | FLTC | DIGITAL |  | IT60 (DJ60) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00609_52ML | 045 | DJGUL00609_ | 52ML | DIGITAL |  | IT60 (DJ60) | 52 DISJ. MOLA | CARREGADA;DESCARREGADA;0;3 | 0;1;2;3 | CARREGADA | DESCARREGADA |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00609_BAIS | 045 | DJGUL00609_ | BAIS | DIGITAL |  | IT60 (DJ60) | 52 DJ BOBINA DE ABERT | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00109
045DJGUL00609_0EST | 045 | DJGUL00609_ | 0EST | COMANDO / DIGITAL | SUBSTITUIR ESTADO DE SIMPLES P/ DUPLO | IT60 (DJ60) | DISJUNTOR | TRANSIÇÃO;ABERTO;FECHADO;INVALIDO | 0;1;2;3 | TRANSIÇÃO | ABERTO | FECHADO | INVALIDO | Discrete | Double-Bit |  | Multibit | 2077;2078 | BRK_045DJGUL00109
045DJGUL00609_FLTC | 045 | DJGUL00609_ | FLTC | DIGITAL |  | IT60 (DJ60) | 52 DISJ TENSAO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGUL00609_0EXT | 045 | DJGUL00609_ | 0EXT | DIGITAL |  | IT60 (DJ60) | DISJUNTOR | INSERIDO;EXTRAÍDO;; | 0;1;2;3 | INSERIDO | EXTRAÍDO
045DJGUL00609_UCGS | 045 | DJGUL00609_ | UCGS | DIGITAL |  | IT60 (DJ60) | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGUL00609_00DF | 045 | DJGUL00609_ | 00DF | DIGITAL |  | IT60 (DJ60) | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGUL00609_00LR | 045 | DJGUL00609_ | 00LR | DIGITAL |  | IT60 (DJ60) | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO
045DJGUL00609_NMFL | 045 | DJGUL00609_ | NMFL | DIGITAL |  | IT60 (DJ60) | UCP-CTRL/PROT/AQUIS. - COM | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGULGERL9_086D | 045 | DJGULGERL9_ | 086D | DIGITAL |  | GERAL (BARRA 88KV) | 86 CIRC. ABER CR BA 88kV | NORMAL; DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGULGERL9_R086 | 045 | DJGULGERL9_ | R086 | COMANDO |  | GERAL (BARRA 88KV) | 86 RELÉ CR BA 88kV | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 702 | Single-Bit | 2185 | GERAL_GUL
045DJGULGERL9_LCBB | 045 | DJGULGERL9_ | LCBB | DIGITAL |  | GERAL (BARRA 88KV) | CHAVE BOIA | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 892 |  |  | GERAL_GUL
045DJGULGERL9_BTLG | 045 | DJGULGERL9_ | BTLG | DIGITAL |  | GERAL (BARRA 88KV) | CH BLOQ TELEC GERAL | ETD;COS;; | 0;1;2;3 | ETD | COS |  |  | Discrete | Single-Bit | 704 |  |  | GERAL_GUL
045DJGULGERL9_CBN1 | 045 | DJGULGERL9_ | CBN1 | DIGITAL |  | GERAL (BARRA 88KV) | CHAVE BOIA - NIVEL 1 | NORMAL;ALARME;0;3 | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 993 |  |  | GERAL_GUL
045DJGULGERL9_CBN1 | 045 | DJGULGERL9_ | CBN1 | DIGITAL |  | GERAL (BARRA 88KV) | CHAVE BOIA - NIVEL 2 | NORMAL;ALARME;0;3 | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 993 |  |  | GERAL_GUL
045DJGULGERL9_FTCA | 045 | DJGULGERL9_ | FTCA | DIGITAL |  | GERAL (BARRA 88KV) | CHAVE BOIA - CA | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA |  |  | Discrete | Single-Bit | 992 |  |  | GERAL_GUL
045DJGULGERL9_FLTC | 045 | DJGULGERL9_ | FLTC | DIGITAL |  | SERV.AUX.GERAL (SAG) | FALTA CC - QTA | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGULGERL9_EEST | 045 | DJGULGERL9_ | EEST | DIGITAL |  | SERV.AUX.GERAL (SAG) | GPS | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045DJGULGERL9_FLTC | 045 | DJGULGERL9_ | FLTC | DIGITAL |  | SERV.AUX.GERAL (SAG) | PAINEL MED FAT - TENSÃO CC | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGULGERL9_CCBX | 045 | DJGULGERL9_ | CCBX | DIGITAL |  | RET1 | RETIFICADOR 1 TENSÃO CC | NORMAL;BAIXA;; | 0;1;2;3 | NORMAL | BAIXA
045DJGULGERL9_CCBX | 045 | DJGULGERL9_ | CCBX | DIGITAL |  | RET2 | RETIFICADOR 2 TENSÃO CC | NORMAL;BAIXA;; | 0;1;2;3 | NORMAL | BAIXA
045DJGULGERL9_ALRM | 045 | DJGULGERL9_ | ALRM | DIGITAL |  | SERV.AUX.GERAL (SAG) | SENSOR FUMAÇA | NORMAL;ALARME | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 714 |  |  | GERAL_GUL
045DJGULGERL9_CASE | 045 | DJGULGERL9_ | CASE | DIGITAL |  | SERV.AUX.GERAL (SAG) | SERVIÇOS AUXILIARES CA | NORMAL;TRANSFERIDO;; | 0;1;2;3 | NORMAL | TRANSFERIDO
045DJGULGERL9_00DF | 045 | DJGULGERL9_ | 00DF | DIGITAL |  | GERAL | SWITCH 01 | NORMAL; DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGULGERL9_00DF | 045 | DJGULGERL9_ | 00DF | DIGITAL |  | GERAL | SWITCH 02 | NORMAL; DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGULGERL9_00DF | 045 | DJGULGERL9_ | 00DF | DIGITAL |  | GERAL | SWITCH 03 | NORMAL; DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGULGERL9_00DF | 045 | DJGULGERL9_ | 00DF | DIGITAL |  | GERAL | SWITCH 04 | NORMAL; DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGULGERL9_00DF | 045 | DJGULGERL9_ | 00DF | DIGITAL |  | GERAL | SWITCH 05 | NORMAL; DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGULGERL9_00DF | 045 | DJGULGERL9_ | 00DF | DIGITAL |  | GERAL | SWITCH 06 | NORMAL; DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045DJGULGERL9_CCBX | 045 | DJGULGERL9_ | CCBX | DIGITAL |  | SERV.AUX.GERAL (SAG) | TENSÃO SISTEMA CC - NÍVEL CRÍTICO | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGULGERL9_FLTA | 045 | DJGULGERL9_ | FLTA | DIGITAL |  | SERV. AUX. 1 (SAX1) | TENSÃO TRSA-1 | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGULGERL9_FLTA | 045 | DJGULGERL9_ | FLTA | DIGITAL |  | SERV. AUX. 2 (SAX2) | TENSÃO TRSA-2 | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGULGERL9_FLTA | 045 | DJGULGERL9_ | FLTA | DIGITAL |  | SERV. AUX.3 (SAX3) | TENSÃO TRSA-3 | NORMAL;FALTA;; | 0;1;2;3 | NORMAL | FALTA
045DJGULGERL9_T12M | 045 | DJGULGERL9_ | T12M | DIGITAL |  | GERAL (BARRA 88KV) | TRANSF. AUTOM. B1>>B2 88KV | NORMAL; MAL SUCEDIDA;; | 0;1;2;3 | NORMAL | MAL SUCEDIDA |  |  | D
045DJGULGERL9_T12S | 045 | DJGULGERL9_ | T12S | DIGITAL |  | GERAL (BARRA 88KV) | TRANSF. AUTOM. B1>>B2 88KV | NORMAL; BEM SUCEDIDA;; | 0;1;2;3 | NORMAL | BEM SUCEDIDA
045DJGULGERL9_T12E | 045 | DJGULGERL9_ | T12E | DIGITAL |  | GERAL (BARRA 88KV) | TRANSF. AUTOM. B1->B2 88KV | NORMAL;EM CURSO;; | 0;1;2;3 | NORMAL | EM CURSO |  |  | Discrete | Double-Bit | 716 |  |  | GERAL_GUL
045DJGULGERL9_T21M | 045 | DJGULGERL9_ | T21M | DIGITAL |  | GERAL (BARRA 88KV) | TRANSF. AUTOM. B2>>B1 88KV | NORMAL; MAL SUCEDIDA;; | 0;1;2;3 | NORMAL | MAL SUCEDIDA
045DJGULGERL9_T21S | 045 | DJGULGERL9_ | T21S | DIGITAL |  | GERAL (BARRA 88KV) | TRANSF. AUTOM. B2>>B1 88KV | NORMAL; BEM SUCEDIDA;; | 0;1;2;3 | NORMAL | BEM SUCEDIDA
045DJGULGERL9_T21E | 045 | DJGULGERL9_ | T21E | DIGITAL |  | GERAL (BARRA 88KV) | TRANSF. AUTOM. 88KV | NORMAL; EM CURSO;; | 0;1;2;3 | NORMAL | EM CURSO
045DJGULGERL9_00TA | 045 | DJGULGERL9_ | 00TA | COMANDO |  | GERAL (BARRA 88KV) | TRANSF. AUTOM. BA 88KV | BLOQUEADO;ATIVADO;; | 0;1;2;3 | BLOQUEADO | ATIVADO |  |  | Discrete | Single-Bit | 717 | Multibit | 2188;2189 | GERAL_GUL
045DJGULGERL9_00DF | 045 | DJGULGERL9_ | 00DF | DIGITAL |  | GERAL | UCC 03 - RTAC | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 708 |  |  | GERAL_GUL
045DJGULSGERL_027I | 045 | DJGULSGERL_ | 027I | DIGITAL | N2= ELIPSE | SERV.AUX.GERAL (SAG) | CH DE BLOQ INFRA TENSAO | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 721 |  |  | GERAL_GUL
045DJGULSGERL_CNT1 | 045 | DJGULSGERL_ | CNT1 | DIGITAL | N2= ELIPSE | SERV.AUX.GERAL (SAG) | CONTATOR 1 | DESLIGADO;LIGADO;; | 0;1;2;3 | DESLIGADO | LIGADO |  |  | Discrete | Single-Bit | 723 |  |  | GERAL_GUL
045DJGULSGERL_CNT2 | 045 | DJGULSGERL_ | CNT2 | DIGITAL | N2= ELIPSE | SERV.AUX.GERAL (SAG) | CONTATOR 2 | DESLIGADO;LIGADO;; | 0;1;2;3 | DESLIGADO | LIGADO |  |  | Discrete | Single-Bit | 724 |  |  | GERAL_GUL
045DJGULSGERL_CNT3 | 045 | DJGULSGERL_ | CNT3 | DIGITAL | N2= ELIPSE | SERV.AUX.GERAL (SAG) | CONTATOR 3 | DESLIGADO;LIGADO;; | 0;1;2;3 | DESLIGADO | LIGADO |  |  | Discrete | Single-Bit | 725 |  |  | GERAL_GUL
045DJGULSGERL_CNT4 | 045 | DJGULSGERL_ | CNT4 | DIGITAL | N2= ELIPSE | SERV.AUX.GERAL (SAG) | CONTATOR 4 | DESLIGADO;LIGADO;; | 0;1;2;3 | DESLIGADO | LIGADO |  |  | Discrete | Single-Bit | 725 |  |  | GERAL_GUL
045DJGULSGERL_TASA | 045 | DJGULSGERL_ | TASA | DIGITAL | N2= ELIPSE | SERV.AUX.GERAL (SAG) | TRANF. AUTOM SERV. AUX | BLOQUEADA;ATIVADA;; | 1;0;3;2 | ATIVADA | BLOQUEADA |  |  | Discrete | Single-Bit | 726 |  |  | GERAL_GUL
045DJGULTA1T2_T2BS | 045 | DJGULTA1T2_ | T2BS | DIGITAL |  | TA 13,8KV | TR1ITR2 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 968 |  |  | GERAL_GUL
045DJGULTA1T2_T2MS | 045 | DJGULTA1T2_ | T2MS | DIGITAL |  | TA 13,8KV | TR1ITR2 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 969 |  |  | GERAL_GUL
045DJGULTA1T3_T3BS | 045 | DJGULTA1T3_ | T3BS | DIGITAL |  | TA 13,8KV | TR1ITR3 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 970 |  |  | GERAL_GUL
045DJGULTA1T3_T3MS | 045 | DJGULTA1T3_ | T3MS | DIGITAL |  | TA 13,8KV | TR1ITR3 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 971 |  |  | GERAL_GUL
045DJGULTA1T4_T4BS | 045 | DJGULTA1T4_ | T4BS | DIGITAL |  | TA 13,8KV | TR1ITR4 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 972 |  |  | GERAL_GUL
045DJGULTA1T4_T4MS | 045 | DJGULTA1T4_ | T4MS | DIGITAL |  | TA 13,8KV | TR1ITR4 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 973 |  |  | GERAL_GUL
045DJGULTA2T1_T1BS | 045 | DJGULTA2T1_ | T1BS | DIGITAL |  | TA 13,8KV | TR2ITR1 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 974 |  |  | GERAL_GUL
045DJGULTA2T1_T1MS | 045 | DJGULTA2T1_ | T1MS | DIGITAL |  | TA 13,8KV | TR2ITR1 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 975 |  |  | GERAL_GUL
045DJGULTA2T3_T3BS | 045 | DJGULTA2T3_ | T3BS | DIGITAL |  | TA 13,8KV | TR2ITR3 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 976 |  |  | GERAL_GUL
045DJGULTA2T3_T3MS | 045 | DJGULTA2T3_ | T3MS | DIGITAL |  | TA 13,8KV | TR2ITR3 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 977 |  |  | GERAL_GUL
045DJGULTA2T4_T4BS | 045 | DJGULTA2T4_ | T4BS | DIGITAL |  | TA 13,8KV | TR2ITR4 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 978 |  |  | GERAL_GUL
045DJGULTA2T4_T4MS | 045 | DJGULTA2T4_ | T4MS | DIGITAL |  | TA 13,8KV | TR2ITR4 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 979 |  |  | GERAL_GUL
045DJGULTA3T1_T1BS | 045 | DJGULTA3T1_ | T1BS | DIGITAL |  | TA 13,8KV | TR3ITR1 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 980 |  |  | GERAL_GUL
045DJGULTA3T1_T1MS | 045 | DJGULTA3T1_ | T1MS | DIGITAL |  | TA 13,8KV | TR3ITR1 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 981 |  |  | GERAL_GUL
045DJGULTA3T2_T2BS | 045 | DJGULTA3T2_ | T2BS | DIGITAL |  | TA 13,8KV | TR3ITR2 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 982 |  |  | GERAL_GUL
045DJGULTA3T2_T2MS | 045 | DJGULTA3T2_ | T2MS | DIGITAL |  | TA 13,8KV | TR3ITR2 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 983 |  |  | GERAL_GUL
045DJGULTA3T4_T4BS | 045 | DJGULTA3T4_ | T4BS | DIGITAL |  | TA 13,8KV | TR3ITR4 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 984 |  |  | GERAL_GUL
045DJGULTA3T4_T4MS | 045 | DJGULTA3T4_ | T4MS | DIGITAL |  | TA 13,8KV | TR3ITR4 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 985 |  |  | GERAL_GUL
045DJGULTA4T1_T1BS | 045 | DJGULTA4T1_ | T1BS | DIGITAL |  | TA 13,8KV | TR4ITR1 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 986 |  |  | GERAL_GUL
045DJGULTA4T1_T1MS | 045 | DJGULTA4T1_ | T1MS | DIGITAL |  | TA 13,8KV | TR4ITR1 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 987 |  |  | GERAL_GUL
045DJGULTA4T2_T2BS | 045 | DJGULTA4T2_ | T2BS | DIGITAL |  | TA 13,8KV | TR4ITR2 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 988 |  |  | GERAL_GUL
045DJGULTA4T2_T2MS | 045 | DJGULTA4T2_ | T2MS | DIGITAL |  | TA 13,8KV | TR4ITR2 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 989 |  |  | GERAL_GUL
045DJGULTA4T3_T3BS | 045 | DJGULTA4T3_ | T3BS | DIGITAL |  | TA 13,8KV | TR4ITR3 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 990 |  |  | GERAL_GUL
045DJGULTA4T3_T3MS | 045 | DJGULTA4T3_ | T3MS | DIGITAL |  | TA 13,8KV | TR4ITR3 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 991 |  |  | GERAL_GUL
045DJGULTAGRL_0TT1 | 045 | DJGULTAGRL_ | 0TT1 | COMANDO |  | TA 13,8KV | TA TR1 | BLOQUEADO;SERVIÇO;; | 1;0;2;3 | SERVIÇO | BLOQUEADO |  |  | Discrete | Single-Bit | 756 | Multibit | 2236;2235 | GERAL_GUL | TRANSFERENCIA AUTOMATICA INVERTIDO
045DJGULTAGRL_0TT2 | 045 | DJGULTAGRL_ | 0TT2 | COMANDO |  | TA 13,8KV | TA TR2 | BLOQUEADO;SERVIÇO;; | 1;0;2;3 | SERVIÇO | BLOQUEADO |  |  | Discrete | Single-Bit | 760 | Multibit | 2244;2243 | GERAL_GUL | TRANSFERENCIA AUTOMATICA INVERTIDO
045DJGULTAGRL_0TT3 | 045 | DJGULTAGRL_ | 0TT3 | COMANDO |  | TA 13,8KV | TA TR3 | BLOQUEADO;SERVIÇO;; | 1;0;2;3 | SERVIÇO | BLOQUEADO |  |  | Discrete | Single-Bit | 764 | Multibit | 2252;2251 | GERAL_GUL | TRANSFERENCIA AUTOMATICA INVERTIDO
045DJGULTAGRL_0TT4 | 045 | DJGULTAGRL_ | 0TT4 | COMANDO |  | TA 13,8KV | TA TR4 | BLOQUEADO;SERVIÇO;; | 1;0;2;3 | SERVIÇO | BLOQUEADO |  |  | Discrete | Single-Bit | 768 | Multibit | 2260;2259 | GERAL_GUL | TRANSFERENCIA AUTOMATICA INVERTIDO
045DJGULTATR1_T1BS | 045 | DJGULTATR1_ | T1BS | DIGITAL |  | TA 13,8KV | TR1 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 960 |  |  | GERAL_GUL
045DJGULTATR1_T1MS | 045 | DJGULTATR1_ | T1MS | DIGITAL |  | TA 13,8KV | TR1 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 961 |  |  | GERAL_GUL
045DJGULTATR2_T2BS | 045 | DJGULTATR2_ | T2BS | DIGITAL |  | TA 13,8KV | TR2 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 962 |  |  | GERAL_GUL
045DJGULTATR2_T2MS | 045 | DJGULTATR2_ | T2MS | DIGITAL |  | TA 13,8KV | TR2 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 963 |  |  | GERAL_GUL
045DJGULTATR3_T3BS | 045 | DJGULTATR3_ | T3BS | DIGITAL |  | TA 13,8KV | TR3 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 964 |  |  | GERAL_GUL
045DJGULTATR3_T3MS | 045 | DJGULTATR3_ | T3MS | DIGITAL |  | TA 13,8KV | TR3 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 965 |  |  | GERAL_GUL
045DJGULTATR4_T4BS | 045 | DJGULTATR4_ | T4BS | DIGITAL |  | TA 13,8KV | TR4 TA BEM SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 966 |  |  | GERAL_GUL
045DJGULTATR4_T4MS | 045 | DJGULTATR4_ | T4MS | DIGITAL |  | TA 13,8KV | TR4 TA MAL SUC. | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 967 |  |  | GERAL_GUL
045DJGULTM1T2_1IT2 | 045 | DJGULTM1T2_ | 1IT2 | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/ TR2 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 894 |  |  | GERAL_GUL
045DJGULTM1T3_1IT3 | 045 | DJGULTM1T3_ | 1IT3 | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/ TR3 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 895 |  |  | GERAL_GUL
045DJGULTM1T4_1IT4 | 045 | DJGULTM1T4_ | 1IT4 | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/ TR4 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 896 |  |  | GERAL_GUL
045DJGULTM2T1_2IT1 | 045 | DJGULTM2T1_ | 2IT1 | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/ TR1 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 898 |  |  | GERAL_GUL
045DJGULTM2T3_2IT3 | 045 | DJGULTM2T3_ | 2IT3 | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/ TR3 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 899 |  |  | GERAL_GUL
045DJGULTM2T3_4IT3 | 045 | DJGULTM2T3_ | 4IT3 | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR3 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 908 |  |  | GERAL_GUL
045DJGULTM2T4_2IT4 | 045 | DJGULTM2T4_ | 2IT4 | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/ TR4 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 900 |  |  | GERAL_GUL
045DJGULTM3T1_3IT1 | 045 | DJGULTM3T1_ | 3IT1 | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/ TR1 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 902 |  |  | GERAL_GUL
045DJGULTM3T2_3IT2 | 045 | DJGULTM3T2_ | 3IT2 | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/ TR2 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 903 |  |  | GERAL_GUL
045DJGULTM3T4_3IT4 | 045 | DJGULTM3T4_ | 3IT4 | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/ TR4 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 904 |  |  | GERAL_GUL
045DJGULTM4T1_4IT1 | 045 | DJGULTM4T1_ | 4IT1 | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR1 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 906 |  |  | GERAL_GUL
045DJGULTM4T2_4IT2 | 045 | DJGULTM4T2_ | 4IT2 | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR2 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 907 |  |  | GERAL_GUL
045DJGULTMBN1_1A4A | 045 | DJGULTMBN1_ | 1A4A | DIGITAL |  | NORMALIZ 13,8KV | NORM. B1A / B4A | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 950 |  |  | GERAL_GUL
045DJGULTMBN2_2B3A | 045 | DJGULTMBN2_ | 2B3A | DIGITAL |  | NORMALIZ 13,8KV | NORM. B2B / B3A | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 951 |  |  | GERAL_GUL
045DJGULTMBQ2_2B3A | 045 | DJGULTMBQ2_ | 2B3A | DIGITAL |  | TMT 13,8KV | TRANSF. B2B / B3A | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 949 |  |  | GERAL_GUL
045DJGULTMBRL_QTT1 | 045 | DJGULTMBRL_ | QTT1 | DIGITAL |  | TMT 13,8KV | TRANSFERENCIA TR1 | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 909 |  |  | GERAL_GUL
045DJGULTMBRL_QTT2 | 045 | DJGULTMBRL_ | QTT2 | DIGITAL |  | TMT 13,8KV | TRANSFERENCIA TR2 | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 913 |  |  | GERAL_GUL
045DJGULTMBRL_QTT3 | 045 | DJGULTMBRL_ | QTT3 | DIGITAL |  | TMT 13,8KV | TRANSFERENCIA TR3 | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 917 |  |  | GERAL_GUL
045DJGULTMBRL_QTT4 | 045 | DJGULTMBRL_ | QTT4 | DIGITAL |  | TMT 13,8KV | TRANSFERENCIA TR4 | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 921 |  |  | GERAL_GUL
045DJGULTMBT1_QNT1 | 045 | DJGULTMBT1_ | QNT1 | DIGITAL |  | NORMALIZ 13,8KV | NORMALIZACAO TR1 | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 893 |  |  | GERAL_GUL
045DJGULTMBT2_QNT2 | 045 | DJGULTMBT2_ | QNT2 | DIGITAL |  | NORMALIZ 13,8KV | NORMALIZACAO TR2 | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 897 |  |  | GERAL_GUL
045DJGULTMBT3_QNT3 | 045 | DJGULTMBT3_ | QNT3 | DIGITAL |  | NORMALIZ 13,8KV | NORMALIZACAO TR3 | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 901 |  |  | GERAL_GUL
045DJGULTMBT4_QNT4 | 045 | DJGULTMBT4_ | QNT4 | DIGITAL |  | NORMALIZ 13,8KV | NORMALIZACAO TR4 | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 905 |  |  | GERAL_GUL
045DJGULTMN12_T2BS | 045 | DJGULTMN12_ | T2BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR2 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 792 |  |  | GERAL_GUL
045DJGULTMN12_T2MS | 045 | DJGULTMN12_ | T2MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR2 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 793 |  |  | GERAL_GUL
045DJGULTMN12_1IT2 | 045 | DJGULTMN12_ | 1IT2 | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR2 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 791 |  |  | GERAL_GUL
045DJGULTMN13_T3MS | 045 | DJGULTMN13_ | T3MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR3 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 796 |  |  | GERAL_GUL
045DJGULTMN13_1IT3 | 045 | DJGULTMN13_ | 1IT3 | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR3 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 794 |  |  | GERAL_GUL
045DJGULTMN13_T3BS | 045 | DJGULTMN13_ | T3BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR3 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 795 |  |  | GERAL_GUL
045DJGULTMN14_T4MS | 045 | DJGULTMN14_ | T4MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR4 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 799 |  |  | GERAL_GUL
045DJGULTMN14_T4BS | 045 | DJGULTMN14_ | T4BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR4 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 798 |  |  | GERAL_GUL
045DJGULTMN14_1IT4 | 045 | DJGULTMN14_ | 1IT4 | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 C/TR4 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 797 |  |  | GERAL_GUL
045DJGULTMN21_T1MS | 045 | DJGULTMN21_ | T1MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR1 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 805 |  |  | GERAL_GUL
045DJGULTMN21_T1BS | 045 | DJGULTMN21_ | T1BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR1 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 804 |  |  | GERAL_GUL
045DJGULTMN21_2IT1 | 045 | DJGULTMN21_ | 2IT1 | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR1 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 803 |  |  | GERAL_GUL
045DJGULTMN23_T3BS | 045 | DJGULTMN23_ | T3BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR3 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 807 |  |  | GERAL_GUL
045DJGULTMN23_T3MS | 045 | DJGULTMN23_ | T3MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR3 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 808 |  |  | GERAL_GUL
045DJGULTMN23_2IT3 | 045 | DJGULTMN23_ | 2IT3 | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR3 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 806 |  |  | GERAL_GUL
045DJGULTMN24_2IT4 | 045 | DJGULTMN24_ | 2IT4 | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR4 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 809 |  |  | GERAL_GUL
045DJGULTMN24_T4BS | 045 | DJGULTMN24_ | T4BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR4 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 810 |  |  | GERAL_GUL
045DJGULTMN24_T4MS | 045 | DJGULTMN24_ | T4MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 C/TR4 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 811 |  |  | GERAL_GUL
045DJGULTMN31_T1BS | 045 | DJGULTMN31_ | T1BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR1 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 816 |  |  | GERAL_GUL
045DJGULTMN31_T1MS | 045 | DJGULTMN31_ | T1MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR1 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 817 |  |  | GERAL_GUL
045DJGULTMN31_3IT1 | 045 | DJGULTMN31_ | 3IT1 | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR1 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 815 |  |  | GERAL_GUL
045DJGULTMN32_T2MS | 045 | DJGULTMN32_ | T2MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR2 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 820 |  |  | GERAL_GUL
045DJGULTMN32_T2BS | 045 | DJGULTMN32_ | T2BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR2 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 819 |  |  | GERAL_GUL
045DJGULTMN32_3IT2 | 045 | DJGULTMN32_ | 3IT2 | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR2 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 818 |  |  | GERAL_GUL
045DJGULTMN34_T4MS | 045 | DJGULTMN34_ | T4MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR4 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 823 |  |  | GERAL_GUL
045DJGULTMN34_3IT4 | 045 | DJGULTMN34_ | 3IT4 | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR4 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 821 |  |  | GERAL_GUL
045DJGULTMN34_T4BS | 045 | DJGULTMN34_ | T4BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 C/TR4 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 822 |  |  | GERAL_GUL
045DJGULTMN41_T1BS | 045 | DJGULTMN41_ | T1BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR1 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 828 |  |  | GERAL_GUL
045DJGULTMN41_T1MS | 045 | DJGULTMN41_ | T1MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR1 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 829 |  |  | GERAL_GUL
045DJGULTMN41_4IT1 | 045 | DJGULTMN41_ | 4IT1 | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR1 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 827 |  |  | GERAL_GUL
045DJGULTMN42_T2BS | 045 | DJGULTMN42_ | T2BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR2 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 831 |  |  | GERAL_GUL
045DJGULTMN42_T2MS | 045 | DJGULTMN42_ | T2MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR2 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 832 |  |  | GERAL_GUL
045DJGULTMN42_4IT2 | 045 | DJGULTMN42_ | 4IT2 | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR2 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 830 |  |  | GERAL_GUL
045DJGULTMN43_T3BS | 045 | DJGULTMN43_ | T3BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR3 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 834 |  |  | GERAL_GUL
045DJGULTMN43_T3MS | 045 | DJGULTMN43_ | T3MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR3 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 835 |  |  | GERAL_GUL
045DJGULTMN43_4IT3 | 045 | DJGULTMN43_ | 4IT3 | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR3 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 833 |  |  | GERAL_GUL
045DJGULTMNB1_4AMS | 045 | DJGULTMNB1_ | 4AMS | DIGITAL |  | NORMALIZ 13,8KV | NM B1A / B4A | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 953 |  |  | GERAL_GUL
045DJGULTMNB1_4ABS | 045 | DJGULTMNB1_ | 4ABS | DIGITAL |  | NORMALIZ 13,8KV | NM B1A / B4A | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 952 |  |  | GERAL_GUL
045DJGULTMNB2_3AMS | 045 | DJGULTMNB2_ | 3AMS | DIGITAL |  | NORMALIZ 13,8KV | NM B2B / B3A | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 955 |  |  | GERAL_GUL
045DJGULTMNB2_3ABS | 045 | DJGULTMNB2_ | 3ABS | DIGITAL |  | NORMALIZ 13,8KV | NM B2B / B3A | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 954 |  |  | GERAL_GUL
045DJGULTMNRL_T1MS | 045 | DJGULTMNRL_ | T1MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 800 |  |  | GERAL_GUL
045DJGULTMNRL_T1BS | 045 | DJGULTMNRL_ | T1BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 790 |  |  | GERAL_GUL
045DJGULTMNRL_MNT1 | 045 | DJGULTMNRL_ | MNT1 | DIGITAL |  | NORMALIZ 13,8KV | NM TR1 | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 789 |  |  | GERAL_GUL
045DJGULTMNRL_T2BS | 045 | DJGULTMNRL_ | T2BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 802 |  |  | GERAL_GUL
045DJGULTMNRL_T2MS | 045 | DJGULTMNRL_ | T2MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 812 |  |  | GERAL_GUL
045DJGULTMNRL_MNT2 | 045 | DJGULTMNRL_ | MNT2 | DIGITAL |  | NORMALIZ 13,8KV | NM TR2 | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 801 |  |  | GERAL_GUL
045DJGULTMNRL_T3BS | 045 | DJGULTMNRL_ | T3BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 814 |  |  | GERAL_GUL
045DJGULTMNRL_T3MS | 045 | DJGULTMNRL_ | T3MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 824 |  |  | GERAL_GUL
045DJGULTMNRL_MNT3 | 045 | DJGULTMNRL_ | MNT3 | DIGITAL |  | NORMALIZ 13,8KV | NM TR3 | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 813 |  |  | GERAL_GUL
045DJGULTMNRL_T4MS | 045 | DJGULTMNRL_ | T4MS | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 836 |  |  | GERAL_GUL
045DJGULTMNRL_MNT4 | 045 | DJGULTMNRL_ | MNT4 | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 825 |  |  | GERAL_GUL
045DJGULTMNRL_T4BS | 045 | DJGULTMNRL_ | T4BS | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 826 |  |  | GERAL_GUL
045DJGULTMNT4_2B3A | 045 | DJGULTMNT4_ | 2B3A | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR1 IM | REPOUSO;EM CURSO;0;3 | 1;0;2;3 | EM CURSO | REPOUSO |  |  | Discrete | Single-Bit | 947 |  |  | GERAL_GUL
045DJGULTMNT4_1A4A | 045 | DJGULTMNT4_ | 1A4A | DIGITAL |  | NORMALIZ 13,8KV | NM TR4 C/TR1 IM | REPOUSO;EM CURSO;0;3 | 1;0;2;3 | EM CURSO | REPOUSO |  |  | Discrete | Single-Bit | 946 |  |  | GERAL_GUL
045DJGULTMT12_T2MS | 045 | DJGULTMT12_ | T2MS | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR2 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 841 |  |  | GERAL_GUL
045DJGULTMT12_T2BS | 045 | DJGULTMT12_ | T2BS | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR2 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 840 |  |  | GERAL_GUL
045DJGULTMT12_1IT2 | 045 | DJGULTMT12_ | 1IT2 | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR2 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 839 |  |  | GERAL_GUL
045DJGULTMT13_T3BS | 045 | DJGULTMT13_ | T3BS | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR3 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 843 |  |  | GERAL_GUL
045DJGULTMT13_T3MS | 045 | DJGULTMT13_ | T3MS | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR3 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 844 |  |  | GERAL_GUL
045DJGULTMT13_1IT3 | 045 | DJGULTMT13_ | 1IT3 | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR3 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 842 |  |  | GERAL_GUL
045DJGULTMT13_T1BS | 045 | DJGULTMT13_ | T1BS | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR1 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 864 |  |  | GERAL_GUL
045DJGULTMT13_T1MS | 045 | DJGULTMT13_ | T1MS | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR1 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 865 |  |  | GERAL_GUL
045DJGULTMT13_3IT1 | 045 | DJGULTMT13_ | 3IT1 | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR1 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 863 |  |  | GERAL_GUL
045DJGULTMT14_T4MS | 045 | DJGULTMT14_ | T4MS | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR4 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 847 |  |  | GERAL_GUL
045DJGULTMT14_1IT4 | 045 | DJGULTMT14_ | 1IT4 | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR4 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 845 |  |  | GERAL_GUL
045DJGULTMT14_T4BS | 045 | DJGULTMT14_ | T4BS | DIGITAL |  | TMT 13,8KV | TM TR1 C/TR4 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 846 |  |  | GERAL_GUL
045DJGULTMT21_T1BS | 045 | DJGULTMT21_ | T1BS | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR1 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 852 |  |  | GERAL_GUL
045DJGULTMT21_T1MS | 045 | DJGULTMT21_ | T1MS | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR1 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 853 |  |  | GERAL_GUL
045DJGULTMT21_2IT1 | 045 | DJGULTMT21_ | 2IT1 | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR1 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 851 |  |  | GERAL_GUL
045DJGULTMT23_T3MS | 045 | DJGULTMT23_ | T3MS | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR3 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 856 |  |  | GERAL_GUL
045DJGULTMT23_2IT3 | 045 | DJGULTMT23_ | 2IT3 | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR3 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 854 |  |  | GERAL_GUL
045DJGULTMT23_T3BS | 045 | DJGULTMT23_ | T3BS | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR3 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 855 |  |  | GERAL_GUL
045DJGULTMT24_T4BS | 045 | DJGULTMT24_ | T4BS | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR4 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 858 |  |  | GERAL_GUL
045DJGULTMT24_T4MS | 045 | DJGULTMT24_ | T4MS | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR4 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 859 |  |  | GERAL_GUL
045DJGULTMT24_2IT4 | 045 | DJGULTMT24_ | 2IT4 | DIGITAL |  | TMT 13,8KV | TM TR2 C/TR4 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 857 |  |  | GERAL_GUL
045DJGULTMT32_T2BS | 045 | DJGULTMT32_ | T2BS | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR2 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 867 |  |  | GERAL_GUL
045DJGULTMT32_3IT2 | 045 | DJGULTMT32_ | 3IT2 | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR2 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 866 |  |  | GERAL_GUL
045DJGULTMT32_T2MS | 045 | DJGULTMT32_ | T2MS | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR2 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 868 |  |  | GERAL_GUL
045DJGULTMT34_T4MS | 045 | DJGULTMT34_ | T4MS | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR4 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 871 |  |  | GERAL_GUL
045DJGULTMT34_T4BS | 045 | DJGULTMT34_ | T4BS | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR4 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 870 |  |  | GERAL_GUL
045DJGULTMT34_3IT4 | 045 | DJGULTMT34_ | 3IT4 | DIGITAL |  | TMT 13,8KV | TM TR3 C/TR4 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 869 |  |  | GERAL_GUL
045DJGULTMT41_T1MS | 045 | DJGULTMT41_ | T1MS | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR1 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 877 |  |  | GERAL_GUL
045DJGULTMT41_4IT1 | 045 | DJGULTMT41_ | 4IT1 | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR1 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 875 |  |  | GERAL_GUL
045DJGULTMT41_T1BS | 045 | DJGULTMT41_ | T1BS | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR1 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 876 |  |  | GERAL_GUL
045DJGULTMT42_T2MS | 045 | DJGULTMT42_ | T2MS | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR2 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 880 |  |  | GERAL_GUL
045DJGULTMT42_4IT2 | 045 | DJGULTMT42_ | 4IT2 | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR2 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 878 |  |  | GERAL_GUL
045DJGULTMT42_T2BS | 045 | DJGULTMT42_ | T2BS | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR2 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 879 |  |  | GERAL_GUL
045DJGULTMT43_T3MS | 045 | DJGULTMT43_ | T3MS | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR3 IM | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 883 |  |  | GERAL_GUL
045DJGULTMT43_4IT3 | 045 | DJGULTMT43_ | 4IT3 | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR3 IM | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 881 |  |  | GERAL_GUL
045DJGULTMT43_T3BS | 045 | DJGULTMT43_ | T3BS | DIGITAL |  | TMT 13,8KV | TM TR4 C/TR3 IM | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 882 |  |  | GERAL_GUL
045DJGULTMTB1_4ABS | 045 | DJGULTMTB1_ | 4ABS | DIGITAL |  | TMT 13,8KV | TMT B1A / B4A | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 940 |  |  | GERAL_GUL
045DJGULTMTB1_4AMS | 045 | DJGULTMTB1_ | 4AMS | DIGITAL |  | TMT 13,8KV | TMT B1A / B4A | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 941 |  |  | GERAL_GUL
045DJGULTMTB1_1A4A | 045 | DJGULTMTB1_ | 1A4A | DIGITAL |  | TMT 13,8KV | TMT B1A / B4A | REPOUSO;EM CURSO;0;3 | 1;0;2;3 | EM CURSO | REPOUSO |  |  | Discrete | Single-Bit | 944 |  |  | GERAL_GUL
045DJGULTMTB2_3ABS | 045 | DJGULTMTB2_ | 3ABS | DIGITAL |  | TMT 13,8KV | TMT B2B / B3A | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 942 |  |  | GERAL_GUL
045DJGULTMTB2_3AMS | 045 | DJGULTMTB2_ | 3AMS | DIGITAL |  | TMT 13,8KV | TMT B2B / B3A | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 943 |  |  | GERAL_GUL
045DJGULTMTB2_2B3A | 045 | DJGULTMTB2_ | 2B3A | DIGITAL |  | TMT 13,8KV | TMT B2B / B3A | REPOUSO;EM CURSO;0;3 | 1;0;2;3 | EM CURSO | REPOUSO |  |  | Discrete | Single-Bit | 945 |  |  | GERAL_GUL
045DJGULTMTRL_T1MS | 045 | DJGULTMTRL_ | T1MS | DIGITAL |  | TMT 13,8KV | TM TR1 | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 848 |  |  | GERAL_GUL
045DJGULTMTRL_T1BS | 045 | DJGULTMTRL_ | T1BS | DIGITAL |  | TMT 13,8KV | TM TR1 | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 838 |  |  | GERAL_GUL
045DJGULTMTRL_MTT1 | 045 | DJGULTMTRL_ | MTT1 | DIGITAL |  | TMT 13,8KV | TM TR1 | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 837 |  |  | GERAL_GUL
045DJGULTMTRL_T2MS | 045 | DJGULTMTRL_ | T2MS | DIGITAL |  | TMT 13,8KV | TM TR2 | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 860 |  |  | GERAL_GUL
045DJGULTMTRL_MTT2 | 045 | DJGULTMTRL_ | MTT2 | DIGITAL |  | TMT 13,8KV | TM TR2 | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 849 |  |  | GERAL_GUL
045DJGULTMTRL_T2BS | 045 | DJGULTMTRL_ | T2BS | DIGITAL |  | TMT 13,8KV | TM TR2 | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 850 |  |  | GERAL_GUL
045DJGULTMTRL_MTT3 | 045 | DJGULTMTRL_ | MTT3 | DIGITAL |  | TMT 13,8KV | TM TR3 | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 861 |  |  | GERAL_GUL
045DJGULTMTRL_T3BS | 045 | DJGULTMTRL_ | T3BS | DIGITAL |  | TMT 13,8KV | TM TR3 | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 862 |  |  | GERAL_GUL
045DJGULTMTRL_T3MS | 045 | DJGULTMTRL_ | T3MS | DIGITAL |  | TMT 13,8KV | TM TR3 | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 872 |  |  | GERAL_GUL
045DJGULTMTRL_T4BS | 045 | DJGULTMTRL_ | T4BS | DIGITAL |  | TMT 13,8KV | TM TR4 | REPOUSO;BEM SUCEDIDA;; | 0;1;2;3 | REPOUSO | BEM SUCEDIDA |  |  | Discrete | Single-Bit | 874 |  |  | GERAL_GUL
045DJGULTMTRL_MTT4 | 045 | DJGULTMTRL_ | MTT4 | DIGITAL |  | TMT 13,8KV | TM TR4 | REPOUSO;EM CURSO;0;3 | 0;1;2;3 | REPOUSO | EM CURSO |  |  | Discrete | Single-Bit | 873 |  |  | GERAL_GUL
045DJGULTMTRL_T4MS | 045 | DJGULTMTRL_ | T4MS | DIGITAL |  | TMT 13,8KV | TM TR4 | REPOUSO;MAL SUCEDIDA;; | 0;1;2;3 | REPOUSO | MAL SUCEDIDA |  |  | Discrete | Single-Bit | 884 |  |  | GERAL_GUL
045DJGULTQ1T2_1IT2 | 045 | DJGULTQ1T2_ | 1IT2 | DIGITAL |  | TMT 13,8KV | TM TR1 C/ TR2 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 910 |  |  | GERAL_GUL
045DJGULTQ1T3_1IT3 | 045 | DJGULTQ1T3_ | 1IT3 | DIGITAL |  | TMT 13,8KV | TM TR1 C/ TR3 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 911 |  |  | GERAL_GUL
045DJGULTQ1T4_1IT4 | 045 | DJGULTQ1T4_ | 1IT4 | DIGITAL |  | TMT 13,8KV | TM TR1 C/ TR4 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 912 |  |  | GERAL_GUL
045DJGULTQ2T2_2IT1 | 045 | DJGULTQ2T2_ | 2IT1 | DIGITAL |  | TMT 13,8KV | TM TR2 C/ TR1 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 914 |  |  | GERAL_GUL
045DJGULTQ2T3_2IT3 | 045 | DJGULTQ2T3_ | 2IT3 | DIGITAL |  | TMT 13,8KV | TM TR2 C/ TR3 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 915 |  |  | GERAL_GUL
045DJGULTQ2T4_2IT4 | 045 | DJGULTQ2T4_ | 2IT4 | DIGITAL |  | TMT 13,8KV | TM TR2 C/ TR4 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 916 |  |  | GERAL_GUL
045DJGULTQ3T1_3IT1 | 045 | DJGULTQ3T1_ | 3IT1 | DIGITAL |  | TMT 13,8KV | TM TR3 C/ TR1 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 918 |  |  | GERAL_GUL
045DJGULTQ3T2_3IT2 | 045 | DJGULTQ3T2_ | 3IT2 | DIGITAL |  | TMT 13,8KV | TM TR3 C/ TR2 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 919 |  |  | GERAL_GUL
045DJGULTQ3T4_3IT4 | 045 | DJGULTQ3T4_ | 3IT4 | DIGITAL |  | TMT 13,8KV | TM TR3 C/ TR4 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 920 |  |  | GERAL_GUL
045DJGULTQ4T1_4IT1 | 045 | DJGULTQ4T1_ | 4IT1 | DIGITAL |  | TMT 13,8KV | TM TR4 C/ TR1 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 922 |  |  | GERAL_GUL
045DJGULTQ4T2_4IT2 | 045 | DJGULTQ4T2_ | 4IT2 | DIGITAL |  | TMT 13,8KV | TM TR4 C/ TR2 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 923 |  |  | GERAL_GUL
045DJGULTQ4T3_4IT3 | 045 | DJGULTQ4T3_ | 4IT3 | DIGITAL |  | TMT 13,8KV | TM TR4 C/ TR3 IMP. | LIBERADO;BLOQUEADO;; | 0;1;3;2 | LIBERADO | BLOQUEADO |  |  | Discrete | Single-Bit | 924 |  |  | GERAL_GUL
045SAGUL00019_00DF | 045 | SAGUL00019_ | 00DF | DIGITAL |  | RET1 | RETIFICADOR 1 | NORMAL;DEFEITO;2;3 | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 729 |  |  | SA_045SAGUL00019_8552368
045SAGUL00019_0EST | 045 | SAGUL00019_ | 0EST | DIGITAL |  | SERV. AUX. 1 (SAX1) | SECCIONADORA - 6477 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 730 |  |  | SA_045SAGUL00019_8552368
045SAGUL00029_00DF | 045 | SAGUL00029_ | 00DF | DIGITAL |  | RET2 | RETIFICADOR 2 | NORMAL;DEFEITO;2;3 | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 728 |  |  | SA_045SAGUL00029_8552218
045SAGUL00029_0EST | 045 | SAGUL00029_ | 0EST | DIGITAL |  | SERV. AUX. 2 (SAX2) | SECCIONADORA - 6478 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 731 |  |  | SA_045SAGUL00029_8552218
045SAGUL00039_0EST | 045 | SAGUL00039_ | 0EST | DIGITAL |  | SERV. AUX. 3 (SAX3) | SECCIONADORA - 6479 | ABERTO;FECHADO;0;3 | 0;1;2;3 | ABERTO | FECHADO |  |  | Discrete | Single-Bit | 732 |  |  | SA_045SAGUL00039_8553013
045TRGUL00019_026A | 045 | TRGUL00019_ | 026A | DIGITAL |  | TR01 | 26 TEMP OLEO 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 88 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_26A2 | 045 | TRGUL00019_ | 26A2 | DIGITAL |  | TR01 | 26 TEMP ÓLEO 2º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00019_49A1 | 045 | TRGUL00019_ | 49A1 | DIGITAL |  | TR01 | 49 TEMP ENROL 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 89 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_49A2 | 045 | TRGUL00019_ | 49A2 | DIGITAL |  | TR01 | 49 TEMP ENROL 2º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00019_50FA | 045 | TRGUL00019_ | 50FA | DIGITAL |  | TR01 | 50 PROT AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00019_50FB | 045 | TRGUL00019_ | 50FB | DIGITAL |  | TR01 | 50 PROT BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00019_50NE | 045 | TRGUL00019_ | 50NE | DIGITAL |  | TR01 | 50 PROT NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00019_50FV | 045 | TRGUL00019_ | 50FV | DIGITAL |  | TR01 | 50 PROT VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00019_51FA | 045 | TRGUL00019_ | 51FA | DIGITAL |  | TR01 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 62 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_51AP | 045 | TRGUL00019_ | 51AP | DIGITAL | N2= ELIPSE | TR01 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00019_51FB | 045 | TRGUL00019_ | 51FB | DIGITAL |  | TR01 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 63 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_51BP | 045 | TRGUL00019_ | 51BP | DIGITAL | N2= ELIPSE | TR01 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00019_51NE | 045 | TRGUL00019_ | 51NE | DIGITAL |  | TR01 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 65 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_51NP | 045 | TRGUL00019_ | 51NP | DIGITAL | N2= ELIPSE | TR01 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00019_51NX | 045 | TRGUL00019_ | 51NX | DIGITAL |  | TR01 | 51 PROT NE X0 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 66 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_51XP | 045 | TRGUL00019_ | 51XP | DIGITAL | N2= ELIPSE | TR01 | 51 PROT NE X0 | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00019_51FV | 045 | TRGUL00019_ | 51FV | DIGITAL |  | TR01 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 64 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_51VP | 045 | TRGUL00019_ | 51VP | DIGITAL | N2= ELIPSE | TR01 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00019_063X | 045 | TRGUL00019_ | 063X | DIGITAL | N2= ELIPSE | TR01 | 63 RELE AUXILIAR | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00019_R631 | 045 | TRGUL00019_ | R631 | DIGITAL |  | TR01 | 63 RELE GAS 1 EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 67 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_R632 | 045 | TRGUL00019_ | R632 | DIGITAL |  | TR01 | 63 RELE GAS 2 EST | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 68 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_071N | 045 | TRGUL00019_ | 071N | DIGITAL |  | TR01 | 71 NIVEL DE OLEO | NORMAL;ALARME;0;3 | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 69 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_0D71 | 045 | TRGUL00019_ | 0D71 | DIGITAL |  | TR01 | 71 NIVEL OLEO COMUT | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 70 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_R861 | 045 | TRGUL00019_ | R861 | COMANDO |  | TR01 | 86 RELE CR-1 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 73 | Single-Bit | 2025 | TS_045TRGUL00019_8553141
045TRGUL00019_R862 | 045 | TRGUL00019_ | R862 | COMANDO |  | TR01 | 86 RELE CR-2 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 74 | Single-Bit | 2026 | TS_045TRGUL00019_8553141
45TRGUL00019_861D | 045 | TRGUL00019_ | 861D | DIGITAL |  | TR01 | 86 CIRC ABER CR-1 | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit
045TRGUL00019_087N | 045 | TRGUL00019_ | 087N | DIGITAL |  | TR01 | 87 PROT TERRA RESTRITA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 77 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_087A | 045 | TRGUL00019_ | 087A | DIGITAL |  | TR01 | 87 RELE DIFERENCIAL AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 75 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_087B | 045 | TRGUL00019_ | 087B | DIGITAL |  | TR01 | 87 RELE DIFERENCIAL BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 76 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_087V | 045 | TRGUL00019_ | 087V | DIGITAL |  | TR01 | 87 RELE DIFERENCIAL VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_CBTL | 045 | TRGUL00019_ | CBTL | DIGITAL |  | TR01 | CH BLOQ TELEC COMUTADOR | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 79 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_VEBQ | 045 | TRGUL00019_ | VEBQ | DIGITAL |  | TR01 | CH BLOQ TELEC VENTILADOR | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 887 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_0BLQ | 045 | TRGUL00019_ | 0BLQ | COMANDO |  | TR01 | COMANDO AUTOM TAP | ATIVADO;BLOQUEADO;; | 0;1;2;3 | ATIVADO | BLOQUEADO |  |  | Discrete | Double-Bit | 86 | Multibit | 2032;2031 | REGC_RTC_045TRGUL00019_8553141
045TRGUL00019_TAP | 045 | TRGUL00019_ | TAP | COMANDO |  | TR01 | COMANDO MANUAL TAP | Abaixado;Elevado;Erro;Transito | 1;2;0;3 | Elevado | Abaixado | Erro | Transito | Discrete | No Input |  | Multibit | 2029;2030 | RTC_045TRGUL00019_8553141
045TRGUL00019_NMDF | 045 | TRGUL00019_ | NMDF | DIGITAL |  | TR01 | COMUTADOR | NORMAL;DEFEITO;0;3 | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 935 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_CMEC | 045 | TRGUL00019_ | CMEC | DIGITAL |  | TR01 | COMUTADOR | NORMAL;EM CURSO;; | 0;1;2;3 | NORMAL | EM CURSO
045TRGUL00019_CREQ | 045 | TRGUL00019_ | CREQ | DIGITAL | N2= ELIPSE | TR01 | COMUTADOR - MANUTENÇÃO | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045TRGUL00019_UCGS | 045 | TRGUL00019_ | UCGS | DIGITAL |  | TR01 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045TRGUL00019_DPCX | 045 | TRGUL00019_ | DPCX | DIGITAL | N2= ELIPSE | TR01 | DPC RELE AUXILIAR | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00019_00DF | 045 | TRGUL00019_ | 00DF | DIGITAL |  | TR01 | REGULADOR TENSÃO / MONITOR TEMPERATURA | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045TRGUL00019_0DPC | 045 | TRGUL00019_ | 0DPC | DIGITAL |  | TR01 | D ALÍVIO PRES COMUT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 994 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_0DAP | 045 | TRGUL00019_ | 0DAP | DIGITAL |  | TR01 | D ALÍVIO PRESSAO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 80 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_AJCG | 045 | TRGUL00019_ | AJCG | DIGITAL | N2= ELIPSE | TR01 | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO | 0;1;2;3 | NORMAL | ALTERADO
045TRGUL00019_00LR | 045 | TRGUL00019_ | 00LR | DIGITAL |  | TR01 | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 91 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_00DF | 045 | TRGUL00019_ | 00DF | DIGITAL |  | TR01 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 78 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_DJTV | 045 | TRGUL00019_ | DJTV | DIGITAL |  | TR01 | VENT CIRCUITO COMANDO | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 84 |  |  | TS_045TRGUL00019_8553141
045TRGUL00019_VENT | 045 | TRGUL00019_ | VENT | COMANDO |  | TR01 | VENTILADOR | DESLIGADO;LIGADO;; | 0;1;2;3 | DESLIGADO | LIGADO |  |  | Discrete | Single-Bit | 82 | Multibit | 2033;2034 | TS_045TRGUL00019_8553141
045TRGUL00019_ISOL | 045 | TRGUL00019_ | ISOL | DIGITAL |  | TR01 | TRANSFORMADOR | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO
045TRGUL00019_0MNT | 045 | TRGUL00019_ | 0MNT | DIGITAL |  | TR01 | TRANSFORMADOR - MANUTENCAO | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO
045TRGUL00029_026A | 045 | TRGUL00029_ | 026A | DIGITAL |  | TR02 | 26 TEMP OLEO 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 88 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_26A2 | 045 | TRGUL00029_ | 26A2 | DIGITAL |  | TR02 | 26 TEMP ÓLEO 2º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00029_49A1 | 045 | TRGUL00029_ | 49A1 | DIGITAL |  | TR02 | 49 TEMP ENROL 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 89 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_49A2 | 045 | TRGUL00029_ | 49A2 | DIGITAL |  | TR02 | 49 TEMP ENROL 2º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00029_50FA | 045 | TRGUL00029_ | 50FA | DIGITAL |  | TR02 | 50 PROT AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00029_50FB | 045 | TRGUL00029_ | 50FB | DIGITAL |  | TR02 | 50 PROT BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00029_50NE | 045 | TRGUL00029_ | 50NE | DIGITAL |  | TR02 | 50 PROT NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00029_50FV | 045 | TRGUL00029_ | 50FV | DIGITAL |  | TR02 | 50 PROT VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00029_51FA | 045 | TRGUL00029_ | 51FA | DIGITAL |  | TR02 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 62 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_51AP | 045 | TRGUL00029_ | 51AP | DIGITAL | N2= ELIPSE | TR02 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00029_51FB | 045 | TRGUL00029_ | 51FB | DIGITAL |  | TR02 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 63 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_51BP | 045 | TRGUL00029_ | 51BP | DIGITAL | N2= ELIPSE | TR02 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00029_51NE | 045 | TRGUL00029_ | 51NE | DIGITAL |  | TR02 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 65 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_51NP | 045 | TRGUL00029_ | 51NP | DIGITAL | N2= ELIPSE | TR02 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00029_51NX | 045 | TRGUL00029_ | 51NX | DIGITAL |  | TR02 | 51 PROT NE X0 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 66 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_51XP | 045 | TRGUL00029_ | 51XP | DIGITAL | N2= ELIPSE | TR02 | 51 PROT NE X0 | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00029_51FV | 045 | TRGUL00029_ | 51FV | DIGITAL |  | TR02 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 64 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_51VP | 045 | TRGUL00029_ | 51VP | DIGITAL | N2= ELIPSE | TR02 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00029_063X | 045 | TRGUL00029_ | 063X | DIGITAL | N2= ELIPSE | TR02 | 63 RELE AUXILIAR | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00029_R631 | 045 | TRGUL00029_ | R631 | DIGITAL |  | TR02 | 63 RELE GAS 1 EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 67 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_R632 | 045 | TRGUL00029_ | R632 | DIGITAL |  | TR02 | 63 RELE GAS 2 EST | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 68 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_071N | 045 | TRGUL00029_ | 071N | DIGITAL |  | TR02 | 71 NIVEL DE OLEO | NORMAL;ALARME;0;3 | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 69 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_0D71 | 045 | TRGUL00029_ | 0D71 | DIGITAL |  | TR02 | 71 NIVEL OLEO COMUT | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 70 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_R861 | 045 | TRGUL00029_ | R861 | COMANDO |  | TR02 | 86 RELE CR-1 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 73 | Single-Bit | 2025 | TS_045TRGUL00019_8553141
045TRGUL00029_R862 | 045 | TRGUL00029_ | R862 | COMANDO |  | TR02 | 86 RELE CR-2 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 74 | Single-Bit | 2026 | TS_045TRGUL00019_8553141
45TRGUL00029_861D | 045 | TRGUL00029_ | 861D | DIGITAL |  | TR02 | 86 CIRC ABER CR-1 | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit
045TRGUL00029_087N | 045 | TRGUL00029_ | 087N | DIGITAL |  | TR02 | 87 PROT TERRA RESTRITA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 77 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_087A | 045 | TRGUL00029_ | 087A | DIGITAL |  | TR02 | 87 RELE DIFERENCIAL AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 75 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_087B | 045 | TRGUL00029_ | 087B | DIGITAL |  | TR02 | 87 RELE DIFERENCIAL BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 76 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_087V | 045 | TRGUL00029_ | 087V | DIGITAL |  | TR02 | 87 RELE DIFERENCIAL VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_CBTL | 045 | TRGUL00029_ | CBTL | DIGITAL |  | TR02 | CH BLOQ TELEC COMUTADOR | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 79 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_VEBQ | 045 | TRGUL00029_ | VEBQ | DIGITAL |  | TR02 | CH BLOQ TELEC VENTILADOR | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 887 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_0BLQ | 045 | TRGUL00029_ | 0BLQ | COMANDO |  | TR02 | COMANDO AUTOM TAP | ATIVADO;BLOQUEADO;; | 0;1;2;3 | ATIVADO | BLOQUEADO |  |  | Discrete | Double-Bit | 86 | Multibit | 2032;2031 | REGC_RTC_045TRGUL00019_8553141
045TRGUL00029_TAP | 045 | TRGUL00029_ | TAP | COMANDO |  | TR02 | COMANDO MANUAL TAP | Abaixado;Elevado;Erro;Transito | 1;2;0;3 | Elevado | Abaixado | Erro | Transito | Discrete | No Input |  | Multibit | 2029;2030 | RTC_045TRGUL00019_8553141
045TRGUL00029_NMDF | 045 | TRGUL00029_ | NMDF | DIGITAL |  | TR02 | COMUTADOR | NORMAL;DEFEITO;0;3 | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 935 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_CMEC | 045 | TRGUL00029_ | CMEC | DIGITAL |  | TR02 | COMUTADOR | NORMAL;EM CURSO;; | 0;1;2;3 | NORMAL | EM CURSO
045TRGUL00029_CREQ | 045 | TRGUL00029_ | CREQ | DIGITAL | N2= ELIPSE | TR02 | COMUTADOR - MANUTENÇÃO | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045TRGUL00029_UCGS | 045 | TRGUL00029_ | UCGS | DIGITAL |  | TR02 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045TRGUL00029_DPCX | 045 | TRGUL00029_ | DPCX | DIGITAL | N2= ELIPSE | TR02 | DPC RELE AUXILIAR | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00029_00DF | 045 | TRGUL00029_ | 00DF | DIGITAL |  | TR02 | REGULADOR TENSÃO / MONITOR TEMPERATURA | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045TRGUL00029_0DPC | 045 | TRGUL00029_ | 0DPC | DIGITAL |  | TR02 | D ALÍVIO PRES COMUT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 994 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_0DAP | 045 | TRGUL00029_ | 0DAP | DIGITAL |  | TR02 | D ALÍVIO PRESSAO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 80 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_AJCG | 045 | TRGUL00029_ | AJCG | DIGITAL | N2= ELIPSE | TR02 | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO | 0;1;2;3 | NORMAL | ALTERADO
045TRGUL00029_00LR | 045 | TRGUL00029_ | 00LR | DIGITAL |  | TR02 | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 91 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_00DF | 045 | TRGUL00029_ | 00DF | DIGITAL |  | TR02 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 78 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_DJTV | 045 | TRGUL00029_ | DJTV | DIGITAL |  | TR02 | VENT CIRCUITO COMANDO | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 84 |  |  | TS_045TRGUL00019_8553141
045TRGUL00029_VENT | 045 | TRGUL00029_ | VENT | COMANDO |  | TR02 | VENTILADOR | DESLIGADO;LIGADO;; | 0;1;2;3 | DESLIGADO | LIGADO |  |  | Discrete | Single-Bit | 82 | Multibit | 2033;2034 | TS_045TRGUL00019_8553141
045TRGUL00029_ISOL | 045 | TRGUL00029_ | ISOL | DIGITAL |  | TR02 | TRANSFORMADOR | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO
045TRGUL00029_0MNT | 045 | TRGUL00029_ | 0MNT | DIGITAL |  | TR02 | TRANSFORMADOR - MANUTENCAO | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO
045TRGUL00039_026A | 045 | TRGUL00039_ | 026A | DIGITAL |  | TR03 | 26 TEMP OLEO 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 88 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_26A2 | 045 | TRGUL00039_ | 26A2 | DIGITAL |  | TR03 | 26 TEMP ÓLEO 2º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00039_49A1 | 045 | TRGUL00039_ | 49A1 | DIGITAL |  | TR03 | 49 TEMP ENROL 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 89 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_49A2 | 045 | TRGUL00039_ | 49A2 | DIGITAL |  | TR03 | 49 TEMP ENROL 2º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00039_50FA | 045 | TRGUL00039_ | 50FA | DIGITAL |  | TR03 | 50 PROT AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00039_50FB | 045 | TRGUL00039_ | 50FB | DIGITAL |  | TR03 | 50 PROT BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00039_50NE | 045 | TRGUL00039_ | 50NE | DIGITAL |  | TR03 | 50 PROT NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00039_50FV | 045 | TRGUL00039_ | 50FV | DIGITAL |  | TR03 | 50 PROT VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00039_51FA | 045 | TRGUL00039_ | 51FA | DIGITAL |  | TR03 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 62 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_51AP | 045 | TRGUL00039_ | 51AP | DIGITAL | N2= ELIPSE | TR03 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00039_51FB | 045 | TRGUL00039_ | 51FB | DIGITAL |  | TR03 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 63 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_51BP | 045 | TRGUL00039_ | 51BP | DIGITAL | N2= ELIPSE | TR03 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00039_51NE | 045 | TRGUL00039_ | 51NE | DIGITAL |  | TR03 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 65 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_51NP | 045 | TRGUL00039_ | 51NP | DIGITAL | N2= ELIPSE | TR03 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00039_51NX | 045 | TRGUL00039_ | 51NX | DIGITAL |  | TR03 | 51 PROT NE X0 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 66 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_51XP | 045 | TRGUL00039_ | 51XP | DIGITAL | N2= ELIPSE | TR03 | 51 PROT NE X0 | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00039_51FV | 045 | TRGUL00039_ | 51FV | DIGITAL |  | TR03 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 64 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_51VP | 045 | TRGUL00039_ | 51VP | DIGITAL | N2= ELIPSE | TR03 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00039_063X | 045 | TRGUL00039_ | 063X | DIGITAL | N2= ELIPSE | TR03 | 63 RELE AUXILIAR | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00039_R631 | 045 | TRGUL00039_ | R631 | DIGITAL |  | TR03 | 63 RELE GAS 1 EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 67 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_R632 | 045 | TRGUL00039_ | R632 | DIGITAL |  | TR03 | 63 RELE GAS 2 EST | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 68 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_071N | 045 | TRGUL00039_ | 071N | DIGITAL |  | TR03 | 71 NIVEL DE OLEO | NORMAL;ALARME;0;3 | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 69 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_0D71 | 045 | TRGUL00039_ | 0D71 | DIGITAL |  | TR03 | 71 NIVEL OLEO COMUT | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 70 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_R861 | 045 | TRGUL00039_ | R861 | COMANDO |  | TR03 | 86 RELE CR-1 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 73 | Single-Bit | 2025 | TS_045TRGUL00019_8553141
045TRGUL00039_R862 | 045 | TRGUL00039_ | R862 | COMANDO |  | TR03 | 86 RELE CR-2 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 74 | Single-Bit | 2026 | TS_045TRGUL00019_8553141
45TRGUL00039_861D | 045 | TRGUL00039_ | 861D | DIGITAL |  | TR03 | 86 CIRC ABER CR-1 | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit
045TRGUL00039_087N | 045 | TRGUL00039_ | 087N | DIGITAL |  | TR03 | 87 PROT TERRA RESTRITA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 77 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_087A | 045 | TRGUL00039_ | 087A | DIGITAL |  | TR03 | 87 RELE DIFERENCIAL AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 75 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_087B | 045 | TRGUL00039_ | 087B | DIGITAL |  | TR03 | 87 RELE DIFERENCIAL BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 76 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_087V | 045 | TRGUL00039_ | 087V | DIGITAL |  | TR03 | 87 RELE DIFERENCIAL VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_CBTL | 045 | TRGUL00039_ | CBTL | DIGITAL |  | TR03 | CH BLOQ TELEC COMUTADOR | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 79 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_VEBQ | 045 | TRGUL00039_ | VEBQ | DIGITAL |  | TR03 | CH BLOQ TELEC VENTILADOR | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 887 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_0BLQ | 045 | TRGUL00039_ | 0BLQ | COMANDO |  | TR03 | COMANDO AUTOM TAP | ATIVADO;BLOQUEADO;; | 0;1;2;3 | ATIVADO | BLOQUEADO |  |  | Discrete | Double-Bit | 86 | Multibit | 2032;2031 | REGC_RTC_045TRGUL00019_8553141
045TRGUL00039_TAP | 045 | TRGUL00039_ | TAP | COMANDO |  | TR03 | COMANDO MANUAL TAP | Abaixado;Elevado;Erro;Transito | 1;2;0;3 | Elevado | Abaixado | Erro | Transito | Discrete | No Input |  | Multibit | 2029;2030 | RTC_045TRGUL00019_8553141
045TRGUL00039_NMDF | 045 | TRGUL00039_ | NMDF | DIGITAL |  | TR03 | COMUTADOR | NORMAL;DEFEITO;0;3 | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 935 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_CMEC | 045 | TRGUL00039_ | CMEC | DIGITAL |  | TR03 | COMUTADOR | NORMAL;EM CURSO;; | 0;1;2;3 | NORMAL | EM CURSO
045TRGUL00039_CREQ | 045 | TRGUL00039_ | CREQ | DIGITAL | N2= ELIPSE | TR03 | COMUTADOR - MANUTENÇÃO | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045TRGUL00039_UCGS | 045 | TRGUL00039_ | UCGS | DIGITAL |  | TR03 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045TRGUL00039_DPCX | 045 | TRGUL00039_ | DPCX | DIGITAL | N2= ELIPSE | TR03 | DPC RELE AUXILIAR | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00039_00DF | 045 | TRGUL00039_ | 00DF | DIGITAL |  | TR03 | REGULADOR TENSÃO / MONITOR TEMPERATURA | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045TRGUL00039_0DPC | 045 | TRGUL00039_ | 0DPC | DIGITAL |  | TR03 | D ALÍVIO PRES COMUT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 994 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_0DAP | 045 | TRGUL00039_ | 0DAP | DIGITAL |  | TR03 | D ALÍVIO PRESSAO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 80 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_AJCG | 045 | TRGUL00039_ | AJCG | DIGITAL | N2= ELIPSE | TR03 | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO | 0;1;2;3 | NORMAL | ALTERADO
045TRGUL00039_00LR | 045 | TRGUL00039_ | 00LR | DIGITAL |  | TR03 | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 91 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_00DF | 045 | TRGUL00039_ | 00DF | DIGITAL |  | TR03 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 78 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_DJTV | 045 | TRGUL00039_ | DJTV | DIGITAL |  | TR03 | VENT CIRCUITO COMANDO | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 84 |  |  | TS_045TRGUL00019_8553141
045TRGUL00039_VENT | 045 | TRGUL00039_ | VENT | COMANDO |  | TR03 | VENTILADOR | DESLIGADO;LIGADO;; | 0;1;2;3 | DESLIGADO | LIGADO |  |  | Discrete | Single-Bit | 82 | Multibit | 2033;2034 | TS_045TRGUL00019_8553141
045TRGUL00039_ISOL | 045 | TRGUL00039_ | ISOL | DIGITAL |  | TR03 | TRANSFORMADOR | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO
045TRGUL00039_0MNT | 045 | TRGUL00039_ | 0MNT | DIGITAL |  | TR03 | TRANSFORMADOR - MANUTENCAO | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO
045TRGUL00049_026A | 045 | TRGUL00049_ | 026A | DIGITAL |  | TR04 | 26 TEMP OLEO 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 88 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_26A2 | 045 | TRGUL00049_ | 26A2 | DIGITAL |  | TR04 | 26 TEMP ÓLEO 2º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00049_49A1 | 045 | TRGUL00049_ | 49A1 | DIGITAL |  | TR04 | 49 TEMP ENROL 1º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 89 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_49A2 | 045 | TRGUL00049_ | 49A2 | DIGITAL |  | TR04 | 49 TEMP ENROL 2º EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00049_50FA | 045 | TRGUL00049_ | 50FA | DIGITAL |  | TR04 | 50 PROT AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00049_50FB | 045 | TRGUL00049_ | 50FB | DIGITAL |  | TR04 | 50 PROT BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00049_50NE | 045 | TRGUL00049_ | 50NE | DIGITAL |  | TR04 | 50 PROT NE | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00049_50FV | 045 | TRGUL00049_ | 50FV | DIGITAL |  | TR04 | 50 PROT VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045TRGUL00049_51FA | 045 | TRGUL00049_ | 51FA | DIGITAL |  | TR04 | 51 PROT AZ | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 62 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_51AP | 045 | TRGUL00049_ | 51AP | DIGITAL | N2= ELIPSE | TR04 | 51 PROT AZ | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00049_51FB | 045 | TRGUL00049_ | 51FB | DIGITAL |  | TR04 | 51 PROT BR | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 63 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_51BP | 045 | TRGUL00049_ | 51BP | DIGITAL | N2= ELIPSE | TR04 | 51 PROT BR | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00049_51NE | 045 | TRGUL00049_ | 51NE | DIGITAL |  | TR04 | 51 PROT NE | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 65 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_51NP | 045 | TRGUL00049_ | 51NP | DIGITAL | N2= ELIPSE | TR04 | 51 PROT NE | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00049_51NX | 045 | TRGUL00049_ | 51NX | DIGITAL |  | TR04 | 51 PROT NE X0 | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 66 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_51XP | 045 | TRGUL00049_ | 51XP | DIGITAL | N2= ELIPSE | TR04 | 51 PROT NE X0 | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00049_51FV | 045 | TRGUL00049_ | 51FV | DIGITAL |  | TR04 | 51 PROT VM | NORMAL;ATUADO;0;3 | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 64 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_51VP | 045 | TRGUL00049_ | 51VP | DIGITAL | N2= ELIPSE | TR04 | 51 PROT VM | NORMAL;PARTIDA;; | 0;1;2;3 | NORMAL | PARTIDA
045TRGUL00049_063X | 045 | TRGUL00049_ | 063X | DIGITAL | N2= ELIPSE | TR04 | 63 RELE AUXILIAR | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00049_R631 | 045 | TRGUL00049_ | R631 | DIGITAL |  | TR04 | 63 RELE GAS 1 EST | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 67 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_R632 | 045 | TRGUL00049_ | R632 | DIGITAL |  | TR04 | 63 RELE GAS 2 EST | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 68 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_071N | 045 | TRGUL00049_ | 071N | DIGITAL |  | TR04 | 71 NIVEL DE OLEO | NORMAL;ALARME;0;3 | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 69 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_0D71 | 045 | TRGUL00049_ | 0D71 | DIGITAL |  | TR04 | 71 NIVEL OLEO COMUT | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 70 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_R861 | 045 | TRGUL00049_ | R861 | COMANDO |  | TR04 | 86 RELE CR-1 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 73 | Single-Bit | 2025 | TS_045TRGUL00019_8553141
045TRGUL00049_R862 | 045 | TRGUL00049_ | R862 | COMANDO |  | TR04 | 86 RELE CR-2 | NORMAL;OPERADA;; | 0;1;2;3 | NORMAL | OPERADA |  |  | Discrete | Single-Bit | 74 | Single-Bit | 2026 | TS_045TRGUL00019_8553141
45TRGUL00049_861D | 045 | TRGUL00049_ | 861D | DIGITAL |  | TR04 | 86 CIRC ABER CR-1 | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit
045TRGUL00049_087N | 045 | TRGUL00049_ | 087N | DIGITAL |  | TR04 | 87 PROT TERRA RESTRITA | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 77 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_087A | 045 | TRGUL00049_ | 087A | DIGITAL |  | TR04 | 87 RELE DIFERENCIAL AZ | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 75 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_087B | 045 | TRGUL00049_ | 087B | DIGITAL |  | TR04 | 87 RELE DIFERENCIAL BR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 76 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_087V | 045 | TRGUL00049_ | 087V | DIGITAL |  | TR04 | 87 RELE DIFERENCIAL VM | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit |  |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_CBTL | 045 | TRGUL00049_ | CBTL | DIGITAL |  | TR04 | CH BLOQ TELEC COMUTADOR | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 79 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_VEBQ | 045 | TRGUL00049_ | VEBQ | DIGITAL |  | TR04 | CH BLOQ TELEC VENTILADOR | BLOQUEADO;SERVIÇO;; | 0;1;2;3 | BLOQUEADO | SERVIÇO |  |  | Discrete | Single-Bit | 887 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_0BLQ | 045 | TRGUL00049_ | 0BLQ | COMANDO |  | TR04 | COMANDO AUTOM TAP | ATIVADO;BLOQUEADO;; | 0;1;2;3 | ATIVADO | BLOQUEADO |  |  | Discrete | Double-Bit | 86 | Multibit | 2032;2031 | REGC_RTC_045TRGUL00019_8553141
045TRGUL00049_TAP | 045 | TRGUL00049_ | TAP | COMANDO |  | TR04 | COMANDO MANUAL TAP | Abaixado;Elevado;Erro;Transito | 1;2;0;3 | Elevado | Abaixado | Erro | Transito | Discrete | No Input |  | Multibit | 2029;2030 | RTC_045TRGUL00019_8553141
045TRGUL00049_NMDF | 045 | TRGUL00049_ | NMDF | DIGITAL |  | TR04 | COMUTADOR | NORMAL;DEFEITO;0;3 | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 935 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_CMEC | 045 | TRGUL00049_ | CMEC | DIGITAL |  | TR04 | COMUTADOR | NORMAL;EM CURSO;; | 0;1;2;3 | NORMAL | EM CURSO
045TRGUL00049_CREQ | 045 | TRGUL00049_ | CREQ | DIGITAL | N2= ELIPSE | TR04 | COMUTADOR - MANUTENÇÃO | NORMAL;REQUERIDA;; | 0;1;2;3 | NORMAL | REQUERIDA
045TRGUL00049_UCGS | 045 | TRGUL00049_ | UCGS | DIGITAL |  | TR04 | DISPARO PROTEÇÃO - COMUNICAÇÃO | NORMAL;FALHA;; | 0;1;2;3 | NORMAL | FALHA
045TRGUL00049_DPCX | 045 | TRGUL00049_ | DPCX | DIGITAL | N2= ELIPSE | TR04 | DPC RELE AUXILIAR | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME
045TRGUL00049_00DF | 045 | TRGUL00049_ | 00DF | DIGITAL |  | TR04 | REGULADOR TENSÃO / MONITOR TEMPERATURA | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO
045TRGUL00049_0DPC | 045 | TRGUL00049_ | 0DPC | DIGITAL |  | TR04 | D ALÍVIO PRES COMUT | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO |  |  | Discrete | Single-Bit | 994 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_0DAP | 045 | TRGUL00049_ | 0DAP | DIGITAL |  | TR04 | D ALÍVIO PRESSAO | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit | 80 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_AJCG | 045 | TRGUL00049_ | AJCG | DIGITAL | N2= ELIPSE | TR04 | UCP-AJUSTE PROTEÇÃO / CONFIG. | NORMAL;ALTERADO | 0;1;2;3 | NORMAL | ALTERADO
045TRGUL00049_00LR | 045 | TRGUL00049_ | 00LR | DIGITAL |  | TR04 | UCP-CTRL/PROT/AQUIS. | LOCAL;REMOTO;; | 0;1;2;3 | LOCAL | REMOTO |  |  | Discrete | Single-Bit | 91 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_00DF | 045 | TRGUL00049_ | 00DF | DIGITAL |  | TR04 | UCP-CTRL/PROT/AQUIS. | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 78 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_DJTV | 045 | TRGUL00049_ | DJTV | DIGITAL |  | TR04 | VENT CIRCUITO COMANDO | NORMAL;DEFEITO;; | 0;1;2;3 | NORMAL | DEFEITO |  |  | Discrete | Single-Bit | 84 |  |  | TS_045TRGUL00019_8553141
045TRGUL00049_VENT | 045 | TRGUL00049_ | VENT | COMANDO |  | TR04 | VENTILADOR | DESLIGADO;LIGADO;; | 0;1;2;3 | DESLIGADO | LIGADO |  |  | Discrete | Single-Bit | 82 | Multibit | 2033;2034 | TS_045TRGUL00019_8553141
045TRGUL00049_ISOL | 045 | TRGUL00049_ | ISOL | DIGITAL |  | TR04 | TRANSFORMADOR | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO
045TRGUL00049_0MNT | 045 | TRGUL00049_ | 0MNT | DIGITAL |  | TR04 | TRANSFORMADOR - MANUTENCAO | NORMAL;ISOLADO;; | 0;1;2;3 | NORMAL | ISOLADO
045DJGUL00039_NMFD | 045 | DJGUL00039_ | NMFD | DIGITAL |  | SC11 (DJ03) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00049_NMFD | 045 | DJGUL00049_ | NMFD | DIGITAL |  | SC12 (DJ04) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00059_NMFD | 045 | DJGUL00059_ | NMFD | DIGITAL |  | SC13 (DJ05) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00069_NMFD | 045 | DJGUL00069_ | NMFD | DIGITAL |  | SC14 (DJ06) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00109_NMFD | 045 | DJGUL00109_ | NMFD | DIGITAL |  | IT10 (DJ10) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00209_NMFD | 045 | DJGUL00209_ | NMFD | DIGITAL |  | IT20 (DJ20) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00309_NMFD | 045 | DJGUL00309_ | NMFD | DIGITAL |  | IT30 (DJ30) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00409_NMFD | 045 | DJGUL00409_ | NMFD | DIGITAL |  | IT40 (DJ40) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00509_NMFD | 045 | DJGUL00509_ | NMFD | DIGITAL |  | IT50 (DJ50) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00609_NMFD | 045 | DJGUL00609_ | NMFD | DIGITAL |  | IT60 (DJ60) | 52 FALHA LIGAR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00109_TTFD | 045 | DJGUL00109_ | TTFD | DIGITAL |  | IT10 (DJ10) | 52 FALHA ABRIR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00209_TTFD | 045 | DJGUL00209_ | TTFD | DIGITAL |  | IT20 (DJ20) | 52 FALHA ABRIR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00309_TTFD | 045 | DJGUL00309_ | TTFD | DIGITAL |  | IT30 (DJ30) | 52 FALHA ABRIR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00409_TTFD | 045 | DJGUL00409_ | TTFD | DIGITAL |  | IT40 (DJ40) | 52 FALHA ABRIR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00509_TTFD | 045 | DJGUL00509_ | TTFD | DIGITAL |  | IT50 (DJ50) | 52 FALHA ABRIR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00609_TTFD | 045 | DJGUL00609_ | TTFD | DIGITAL |  | IT60 (DJ60) | 52 FALHA ABRIR DJ | NORMAL;ALARME;; | 0;1;2;3 | NORMAL | ALARME |  |  | Discrete | Single-Bit |  |  |  | BRK_045DJGUL00039
045DJGUL00169_AFDC | 045 | DJGUL00169_ | AFDC | DIGITAL |  | DJ16 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_AFDC | 045 | DJGUL00219_ | AFDC | DIGITAL |  | DJ21 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_AFDC | 045 | DJGUL00229_ | AFDC | DIGITAL |  | DJ22 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_AFDC | 045 | DJGUL00239_ | AFDC | DIGITAL |  | DJ23 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_AFDC | 045 | DJGUL00249_ | AFDC | DIGITAL |  | DJ24 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_AFDC | 045 | DJGUL00259_ | AFDC | DIGITAL |  | DJ25 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_AFDC | 045 | DJGUL00269_ | AFDC | DIGITAL |  | DJ26 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_AFDC | 045 | DJGUL00319_ | AFDC | DIGITAL |  | DJ31 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_AFDC | 045 | DJGUL00329_ | AFDC | DIGITAL |  | DJ32 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_AFDC | 045 | DJGUL00339_ | AFDC | DIGITAL |  | DJ33 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_AFDC | 045 | DJGUL00349_ | AFDC | DIGITAL |  | DJ34 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_AFDC | 045 | DJGUL00359_ | AFDC | DIGITAL |  | DJ35 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_AFDC | 045 | DJGUL00369_ | AFDC | DIGITAL |  | DJ36 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00109_AFDC | 045 | DJGUL00109_ | AFDC | DIGITAL |  | IT10 (DJ10) | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00209_AFDC | 045 | DJGUL00209_ | AFDC | DIGITAL |  | IT20 (DJ20) | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00309_AFDC | 045 | DJGUL00309_ | AFDC | DIGITAL |  | IT30 (DJ30) | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00409_AFDC | 045 | DJGUL00409_ | AFDC | DIGITAL |  | IT40 (DJ40) | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00509_AFDC | 045 | DJGUL00509_ | AFDC | DIGITAL |  | IT50 (DJ50) | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00609_AFDC | 045 | DJGUL00609_ | AFDC | DIGITAL |  | IT60 (DJ60) | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00039_POAB | 045 | DJGUL00039_ | POAB | DIGITAL | N2= ELIPSE | SC11 (DJ03) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00049_POAB | 045 | DJGUL00049_ | POAB | DIGITAL | N2= ELIPSE | SC12 (DJ04) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00059_POAB | 045 | DJGUL00059_ | POAB | DIGITAL | N2= ELIPSE | SC13 (DJ05) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00069_POAB | 045 | DJGUL00069_ | POAB | DIGITAL | N2= ELIPSE | SC14 (DJ06) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00109_POAB | 045 | DJGUL00109_ | POAB | DIGITAL | N2= ELIPSE | IT10 (DJ10) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00209_POAB | 045 | DJGUL00209_ | POAB | DIGITAL | N2= ELIPSE | IT20 (DJ20) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00309_POAB | 045 | DJGUL00309_ | POAB | DIGITAL | N2= ELIPSE | IT30 (DJ30) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00409_POAB | 045 | DJGUL00409_ | POAB | DIGITAL | N2= ELIPSE | IT40 (DJ40) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00509_POAB | 045 | DJGUL00509_ | POAB | DIGITAL | N2= ELIPSE | IT50 (DJ50) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00609_POAB | 045 | DJGUL00609_ | POAB | DIGITAL | N2= ELIPSE | IT60 (DJ60) | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_POAB | 045 | DJGUL00119_ | POAB | DIGITAL | N2= ELIPSE | DJ11 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_POAB | 045 | DJGUL00129_ | POAB | DIGITAL | N2= ELIPSE | DJ12 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00139_POAB | 045 | DJGUL00139_ | POAB | DIGITAL | N2= ELIPSE | DJ13 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_POAB | 045 | DJGUL00149_ | POAB | DIGITAL | N2= ELIPSE | DJ14 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_POAB | 045 | DJGUL00159_ | POAB | DIGITAL | N2= ELIPSE | DJ15 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00169_POAB | 045 | DJGUL00169_ | POAB | DIGITAL | N2= ELIPSE | DJ16 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00219_POAB | 045 | DJGUL00219_ | POAB | DIGITAL | N2= ELIPSE | DJ21 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00229_POAB | 045 | DJGUL00229_ | POAB | DIGITAL | N2= ELIPSE | DJ22 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00239_POAB | 045 | DJGUL00239_ | POAB | DIGITAL | N2= ELIPSE | DJ23 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00249_POAB | 045 | DJGUL00249_ | POAB | DIGITAL | N2= ELIPSE | DJ24 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00259_POAB | 045 | DJGUL00259_ | POAB | DIGITAL | N2= ELIPSE | DJ25 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00269_POAB | 045 | DJGUL00269_ | POAB | DIGITAL | N2= ELIPSE | DJ26 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00319_POAB | 045 | DJGUL00319_ | POAB | DIGITAL | N2= ELIPSE | DJ31 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00329_POAB | 045 | DJGUL00329_ | POAB | DIGITAL | N2= ELIPSE | DJ32 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00339_POAB | 045 | DJGUL00339_ | POAB | DIGITAL | N2= ELIPSE | DJ33 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00349_POAB | 045 | DJGUL00349_ | POAB | DIGITAL | N2= ELIPSE | DJ34 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00359_POAB | 045 | DJGUL00359_ | POAB | DIGITAL | N2= ELIPSE | DJ35 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00369_POAB | 045 | DJGUL00369_ | POAB | DIGITAL | N2= ELIPSE | DJ36 | PORTA ABERTA CUB - TRIP | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00149_AFDC | 045 | DJGUL00149_ | AFDC | DIGITAL |  | DJ14 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00159_AFDC | 045 | DJGUL00159_ | AFDC | DIGITAL |  | DJ15 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00119_AFDC | 045 | DJGUL00119_ | AFDC | DIGITAL |  | DJ11 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO
045DJGUL00129_AFDC | 045 | DJGUL00129_ | AFDC | DIGITAL |  | DJ12 | PROT ARCO - COMPARTIMENTO CABOS - ALIMENTADOR | NORMAL;ATUADO;; | 0;1;2;3 | NORMAL | ATUADO

## ANALOGICAS
Signal Name (TAG) | HLEVEL | Signal Alias (Descritivo) | COMMENT | Device Mapping (Equipamento) | Signal Type | Measurement Type | Display Unit | Phases | Alarm Limits | Remote Point Alias | Remote Point Type | Scaling Factor | Input Coordinate (Endereço da Analógica)
045DJGUL00019_00IA | DJ01 | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00019_00IB | DJ01 | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00019_00IN | DJ01 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00019_00IV | DJ01 | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00019_00FP | DJ01 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00019_00MW | DJ01 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00019_MVAR | DJ01 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00019_0VBC | DJ01 | TENSAO BR | TRATAR NO ELIPSE |  | Custom | Voltage | kV | B
045DJGUL00019_MWHE | DJ01 | ENERGIA ATIVA ENTREGUE |  |  | Measured Value | ACTIVE ENERGY DELIVERED
045DJGUL00019_MRHE | DJ01 | ENERGIA REATIVA ENTREGUE |  |  | Measured Value | REACTIVE ENERGY DELIVERED
045DJGUL00019_0FRQ | DJ01 | FREQUENCIA |  |  | Measured Value | FREQUENCY
045DJGUL00019_0MVA | DJ01 | POT APARENTE |  |  | Measured Value | APPARENT POWER
045DJGUL00019_TMDJ | DJ01 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00019_TADJ | DJ01 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00019_TFDJ | DJ01 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00029_00FP | DJ02 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00029_00IN | DJ02 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00029_00IA | DJ02 | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00029_MVAR | DJ02 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00029_0VBC | DJ02 | TENSAO BR | TRATAR NO ELIPSE |  | Custom | Voltage | kV | B
045DJGUL00029_00IB | DJ02 | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00029_00IV | DJ02 | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00029_00MW | DJ02 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00029_MWHE | DJ02 | ENERGIA ATIVA ENTREGUE |  |  | Measured Value | ACTIVE ENERGY DELIVERED
045DJGUL00029_MRHE | DJ02 | ENERGIA REATIVA ENTREGUE |  |  | Measured Value | REACTIVE ENERGY DELIVERED
045DJGUL00029_0FRQ | DJ02 | FREQUENCIA |  |  | Measured Value | FREQUENCY
045DJGUL00029_0MVA | DJ02 | POT APARENTE |  |  | Measured Value | APPARENT POWER
045DJGUL00029_TMDJ | DJ02 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00029_TADJ | DJ02 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00029_TFDJ | DJ02 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00039_00IA | SC11 (DJ03) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00039_00IB | SC11 (DJ03) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00039_00IN | SC11 (DJ03) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00039_00IV | SC11 (DJ03) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00039_00FP | SC11 (DJ03) | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00039_0FRQ | SC11 (DJ03) | FREQUENCIA |  |  | Measured Value | Frequency | Hz | ABC
045DJGUL00039_0MVA | SC11 (DJ03) | POT APARENTE |  |  | Measured Value | Apparent Power | MVA | ABC
045DJGUL00039_00MW | SC11 (DJ03) | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00039_MVAR | SC11 (DJ03) | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00039_00VA | SC11 (DJ03) | TENSAO AZ |  |  | Measured Value | Voltage | kV | A
045DJGUL00039_00VB | SC11 (DJ03) | TENSAO BR |  |  | Measured Value | Voltage | kV | B
045DJGUL00039_00VV | SC11 (DJ03) | TENSAO VM |  |  | Measured Value | Voltage | kV | C
045DJGUL00039_MWHE | SC11 (DJ03) | ENERGIA ATIVA ENTREGUE |  |  | Measured Value
045DJGUL00039_MWHS | SC11 (DJ03) | ENERGIA ATIVA RECEBIDA |  |  | Measured Value
045DJGUL00039_MRHE | SC11 (DJ03) | ENERGIA REATIVA ENTREGUE |  |  | Measured Value
045DJGUL00039_MRHS | SC11 (DJ03) | ENERGIA REATIVA RECEBIDA |  |  | Measured Value
045DJGUL00039_TMDJ | SC11 (DJ03) | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00039_TADJ | SC11 (DJ03) | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00039_TFDJ | SC11 (DJ03) | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00039_0VAB | SC11 (DJ03) | TENSÃO AZ/BR |  |  | Measured Value
045DJGUL00039_0VBV | SC11 (DJ03) | TENSÃO BR/VM |  |  | Measured Value
045DJGUL00039_0VVA | SC11 (DJ03) | TENSÃO VM/AZ |  |  | Measured Value
045DJGUL00049_MVAR | SC12 (DJ04) | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00049_0FRQ | SC12 (DJ04) | FREQUENCIA |  |  | Measured Value | Frequency | Hz | ABC
045DJGUL00049_00VV | SC12 (DJ04) | TENSAO VM |  |  | Measured Value | Voltage | kV | C
045DJGUL00049_0MVA | SC12 (DJ04) | POT APARENTE |  |  | Measured Value | Apparent Power | MVA | ABC
045DJGUL00049_00VA | SC12 (DJ04) | TENSAO AZ |  |  | Measured Value | Voltage | kV | A
045DJGUL00049_00VB | SC12 (DJ04) | TENSAO BR |  |  | Measured Value | Voltage | kV | B
045DJGUL00049_00MW | SC12 (DJ04) | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00049_00IV | SC12 (DJ04) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00049_00IB | SC12 (DJ04) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00049_00IN | SC12 (DJ04) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00049_00IA | SC12 (DJ04) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00049_00FP | SC12 (DJ04) | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00049_MWHE | SC12 (DJ04) | ENERGIA ATIVA ENTREGUE |  |  | Measured Value
045DJGUL00049_MWHS | SC12 (DJ04) | ENERGIA ATIVA RECEBIDA |  |  | Measured Value
045DJGUL00049_MRHE | SC12 (DJ04) | ENERGIA REATIVA ENTREGUE |  |  | Measured Value
045DJGUL00049_MRHS | SC12 (DJ04) | ENERGIA REATIVA RECEBIDA |  |  | Measured Value
045DJGUL00049_TMDJ | SC12 (DJ04) | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00049_TADJ | SC12 (DJ04) | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00049_TFDJ | SC12 (DJ04) | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00049_0VAB | SC12 (DJ04) | TENSÃO AZ/BR |  |  | Measured Value
045DJGUL00049_0VBV | SC12 (DJ04) | TENSÃO BR/VM |  |  | Measured Value
045DJGUL00049_0VVA | SC12 (DJ04) | TENSÃO VM/AZ |  |  | Measured Value
045DJGUL00059_00IB | SC13 (DJ05) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00059_00FP | SC13 (DJ05) | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00059_00IA | SC13 (DJ05) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00059_MVAR | SC13 (DJ05) | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00059_0FRQ | SC13 (DJ05) | FREQUENCIA |  |  | Measured Value | Frequency | Hz | ABC
045DJGUL00059_00VB | SC13 (DJ05) | TENSAO BR |  |  | Measured Value | Voltage | kV | B
045DJGUL00059_00VA | SC13 (DJ05) | TENSAO AZ |  |  | Measured Value | Voltage | kV | A
045DJGUL00059_00VV | SC13 (DJ05) | TENSAO VM |  |  | Measured Value | Voltage | kV | C
045DJGUL00059_0MVA | SC13 (DJ05) | POT APARENTE |  |  | Measured Value | Apparent Power | MVA | ABC
045DJGUL00059_00IV | SC13 (DJ05) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00059_00MW | SC13 (DJ05) | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00059_00IN | SC13 (DJ05) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00059_MWHE | SC13 (DJ05) | ENERGIA ATIVA ENTREGUE |  |  | Measured Value
045DJGUL00059_MWHS | SC13 (DJ05) | ENERGIA ATIVA RECEBIDA |  |  | Measured Value
045DJGUL00059_MRHE | SC13 (DJ05) | ENERGIA REATIVA ENTREGUE |  |  | Measured Value
045DJGUL00059_MRHS | SC13 (DJ05) | ENERGIA REATIVA RECEBIDA |  |  | Measured Value
045DJGUL00059_TMDJ | SC13 (DJ05) | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00059_TADJ | SC13 (DJ05) | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00059_TFDJ | SC13 (DJ05) | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00059_0VAB | SC13 (DJ05) | TENSÃO AZ/BR |  |  | Measured Value
045DJGUL00059_0VBV | SC13 (DJ05) | TENSÃO BR/VM |  |  | Measured Value
045DJGUL00059_0VVA | SC13 (DJ05) | TENSÃO VM/AZ |  |  | Measured Value
045DJGUL00069_00IV | SC14 (DJ06) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00069_00MW | SC14 (DJ06) | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00069_00VA | SC14 (DJ06) | TENSAO AZ |  |  | Measured Value | Voltage | kV | A
045DJGUL00069_00IN | SC14 (DJ06) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00069_00IB | SC14 (DJ06) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00069_00FP | SC14 (DJ06) | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00069_00IA | SC14 (DJ06) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00069_MVAR | SC14 (DJ06) | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00069_0MVA | SC14 (DJ06) | POT APARENTE |  |  | Measured Value | Apparent Power | MVA | ABC
045DJGUL00069_0FRQ | SC14 (DJ06) | FREQUENCIA |  |  | Measured Value | Frequency | Hz | ABC
045DJGUL00069_00VB | SC14 (DJ06) | TENSAO BR |  |  | Measured Value | Voltage | kV | B
045DJGUL00069_00VV | SC14 (DJ06) | TENSAO VM |  |  | Measured Value | Voltage | kV | C
045DJGUL00069_MWHE | SC14 (DJ06) | ENERGIA ATIVA ENTREGUE |  |  | Measured Value
045DJGUL00069_MWHS | SC14 (DJ06) | ENERGIA ATIVA RECEBIDA |  |  | Measured Value
045DJGUL00069_MRHE | SC14 (DJ06) | ENERGIA REATIVA ENTREGUE |  |  | Measured Value
045DJGUL00069_MRHS | SC14 (DJ06) | ENERGIA REATIVA RECEBIDA |  |  | Measured Value
045DJGUL00069_TMDJ | SC14 (DJ06) | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00069_TADJ | SC14 (DJ06) | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00069_TFDJ | SC14 (DJ06) | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00069_0VAB | SC14 (DJ06) | TENSÃO AZ/BR |  |  | Measured Value
045DJGUL00069_0VBV | SC14 (DJ06) | TENSÃO BR/VM |  |  | Measured Value
045DJGUL00069_0VVA | SC14 (DJ06) | TENSÃO VM/AZ |  |  | Measured Value
045DJGUL00109_00IV | IT10 (DJ10) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00109_00IB | IT10 (DJ10) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00109_00IA | IT10 (DJ10) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00109_00IN | IT10 (DJ10) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00119_00IA | DJ11 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00119_00IB | DJ11 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00119_00IN | DJ11 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00119_00IV | DJ11 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00119_00FP | DJ11 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00119_00MW | DJ11 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00119_MVAR | DJ11 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00119_00VA | DJ11 | TENSAO AZ |  |  | Measured Value
045DJGUL00119_00VB | DJ11 | TENSAO BR |  |  | Measured Value
045DJGUL00119_00VV | DJ11 | TENSAO VM |  |  | Measured Value
045DJGUL00119_0ITA | DJ11 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00119_0ITB | DJ11 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00119_0ITN | DJ11 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00119_0ITV | DJ11 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00119_0MVA | DJ11 | POT APARENTE |  |  | Measured Value
045DJGUL00119_AITA | DJ11 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00119_AITB | DJ11 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00119_AITV | DJ11 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00119_TADJ | DJ11 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00119_TFDJ | DJ11 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00119_TMDJ | DJ11 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00129_00MW | DJ12 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00129_MVAR | DJ12 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00129_00IV | DJ12 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00129_00IN | DJ12 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00129_00IB | DJ12 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00129_00IA | DJ12 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00129_00FP | DJ12 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00129_00VA | DJ12 | TENSAO AZ |  |  | Measured Value
045DJGUL00129_00VB | DJ12 | TENSAO BR |  |  | Measured Value
045DJGUL00129_00VV | DJ12 | TENSAO VM |  |  | Measured Value
045DJGUL00129_0ITA | DJ12 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00129_0ITB | DJ12 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00129_0ITN | DJ12 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00129_0ITV | DJ12 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00129_0MVA | DJ12 | POT APARENTE |  |  | Measured Value
045DJGUL00129_AITA | DJ12 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00129_AITB | DJ12 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00129_AITV | DJ12 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00129_TADJ | DJ12 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00129_TFDJ | DJ12 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00129_TMDJ | DJ12 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00139_MVAR | DJ13 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00139_00MW | DJ13 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00139_00IV | DJ13 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00139_00IN | DJ13 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00139_00IA | DJ13 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00139_00FP | DJ13 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00139_00IB | DJ13 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00139_00VA | DJ13 | TENSAO AZ |  |  | Measured Value
045DJGUL00139_00VB | DJ13 | TENSAO BR |  |  | Measured Value
045DJGUL00139_00VV | DJ13 | TENSAO VM |  |  | Measured Value
045DJGUL00139_0ITA | DJ13 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00139_0ITB | DJ13 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00139_0ITN | DJ13 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00139_0ITV | DJ13 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00139_0MVA | DJ13 | POT APARENTE |  |  | Measured Value
045DJGUL00139_AITA | DJ13 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00139_AITB | DJ13 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00139_AITV | DJ13 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00139_TADJ | DJ13 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00139_TFDJ | DJ13 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00139_TMDJ | DJ13 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00149_00MW | DJ14 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00149_00IV | DJ14 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00149_MVAR | DJ14 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00149_00IB | DJ14 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00149_00IN | DJ14 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00149_00IA | DJ14 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00149_00FP | DJ14 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00149_00VA | DJ14 | TENSAO AZ |  |  | Measured Value
045DJGUL00149_00VB | DJ14 | TENSAO BR |  |  | Measured Value
045DJGUL00149_00VV | DJ14 | TENSAO VM |  |  | Measured Value
045DJGUL00149_0ITA | DJ14 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00149_0ITB | DJ14 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00149_0ITN | DJ14 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00149_0ITV | DJ14 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00149_0MVA | DJ14 | POT APARENTE |  |  | Measured Value
045DJGUL00149_AITA | DJ14 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00149_AITB | DJ14 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00149_AITV | DJ14 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00149_TADJ | DJ14 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00149_TFDJ | DJ14 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00149_TMDJ | DJ14 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00159_MVAR | DJ15 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00159_00MW | DJ15 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00159_00IV | DJ15 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00159_00IN | DJ15 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00159_00IA | DJ15 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00159_00IB | DJ15 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00159_00FP | DJ15 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00159_00VA | DJ15 | TENSAO AZ |  |  | Measured Value
045DJGUL00159_00VB | DJ15 | TENSAO BR |  |  | Measured Value
045DJGUL00159_00VV | DJ15 | TENSAO VM |  |  | Measured Value
045DJGUL00159_0ITA | DJ15 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00159_0ITB | DJ15 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00159_0ITN | DJ15 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00159_0ITV | DJ15 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00159_0MVA | DJ15 | POT APARENTE |  |  | Measured Value
045DJGUL00159_AITA | DJ15 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00159_AITB | DJ15 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00159_AITV | DJ15 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00159_TADJ | DJ15 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00159_TFDJ | DJ15 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00159_TMDJ | DJ15 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00169_MVAR | DJ16 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00169_00IV | DJ16 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00169_00MW | DJ16 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00169_00IN | DJ16 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00169_00IA | DJ16 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00169_00FP | DJ16 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00169_00IB | DJ16 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00169_00VA | DJ16 | TENSAO AZ |  |  | Measured Value
045DJGUL00169_00VB | DJ16 | TENSAO BR |  |  | Measured Value
045DJGUL00169_00VV | DJ16 | TENSAO VM |  |  | Measured Value
045DJGUL00169_0ITA | DJ16 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00169_0ITB | DJ16 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00169_0ITN | DJ16 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00169_0ITV | DJ16 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00169_0MVA | DJ16 | POT APARENTE |  |  | Measured Value
045DJGUL00169_AITA | DJ16 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00169_AITB | DJ16 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00169_AITV | DJ16 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00169_TADJ | DJ16 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00169_TFDJ | DJ16 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00169_TMDJ | DJ16 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00209_00IV | IT20 (DJ20) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00209_00IN | IT20 (DJ20) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00209_00IB | IT20 (DJ20) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00209_00IA | IT20 (DJ20) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00219_00MW | DJ21 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00219_MVAR | DJ21 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00219_00IV | DJ21 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00219_00IN | DJ21 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00219_00IB | DJ21 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00219_00IA | DJ21 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00219_00FP | DJ21 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00219_00VA | DJ21 | TENSAO AZ |  |  | Measured Value
045DJGUL00219_00VB | DJ21 | TENSAO BR |  |  | Measured Value
045DJGUL00219_00VV | DJ21 | TENSAO VM |  |  | Measured Value
045DJGUL00219_0ITA | DJ21 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00219_0ITB | DJ21 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00219_0ITN | DJ21 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00219_0ITV | DJ21 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00219_0MVA | DJ21 | POT APARENTE |  |  | Measured Value
045DJGUL00219_AITA | DJ21 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00219_AITB | DJ21 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00219_AITV | DJ21 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00219_TADJ | DJ21 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00219_TFDJ | DJ21 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00219_TMDJ | DJ21 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00229_MVAR | DJ22 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00229_00IV | DJ22 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00229_00IB | DJ22 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00229_00MW | DJ22 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00229_00IN | DJ22 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00229_00IA | DJ22 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00229_00FP | DJ22 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00229_00VA | DJ22 | TENSAO AZ |  |  | Measured Value
045DJGUL00229_00VB | DJ22 | TENSAO BR |  |  | Measured Value
045DJGUL00229_00VV | DJ22 | TENSAO VM |  |  | Measured Value
045DJGUL00229_0ITA | DJ22 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00229_0ITB | DJ22 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00229_0ITN | DJ22 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00229_0ITV | DJ22 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00229_0MVA | DJ22 | POT APARENTE |  |  | Measured Value
045DJGUL00229_AITA | DJ22 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00229_AITB | DJ22 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00229_AITV | DJ22 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00229_TADJ | DJ22 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00229_TFDJ | DJ22 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00229_TMDJ | DJ22 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00239_00FP | DJ23 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00239_MVAR | DJ23 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00239_00MW | DJ23 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00239_00IV | DJ23 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00239_00IB | DJ23 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00239_00IN | DJ23 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00239_00IA | DJ23 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00239_00VA | DJ23 | TENSAO AZ |  |  | Measured Value
045DJGUL00239_00VB | DJ23 | TENSAO BR |  |  | Measured Value
045DJGUL00239_00VV | DJ23 | TENSAO VM |  |  | Measured Value
045DJGUL00239_0ITA | DJ23 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00239_0ITB | DJ23 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00239_0ITN | DJ23 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00239_0ITV | DJ23 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00239_0MVA | DJ23 | POT APARENTE |  |  | Measured Value
045DJGUL00239_AITA | DJ23 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00239_AITB | DJ23 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00239_AITV | DJ23 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00239_TADJ | DJ23 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00239_TFDJ | DJ23 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00239_TMDJ | DJ23 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00249_MVAR | DJ24 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00249_00MW | DJ24 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00249_00IV | DJ24 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00249_00IN | DJ24 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00249_00IB | DJ24 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00249_00IA | DJ24 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00249_00FP | DJ24 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00249_00VA | DJ24 | TENSAO AZ |  |  | Measured Value
045DJGUL00249_00VB | DJ24 | TENSAO BR |  |  | Measured Value
045DJGUL00249_00VV | DJ24 | TENSAO VM |  |  | Measured Value
045DJGUL00249_0ITA | DJ24 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00249_0ITB | DJ24 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00249_0ITN | DJ24 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00249_0ITV | DJ24 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00249_0MVA | DJ24 | POT APARENTE |  |  | Measured Value
045DJGUL00249_AITA | DJ24 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00249_AITB | DJ24 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00249_AITV | DJ24 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00249_TADJ | DJ24 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00249_TFDJ | DJ24 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00249_TMDJ | DJ24 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00259_MVAR | DJ25 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00259_00MW | DJ25 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00259_00IN | DJ25 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00259_00IA | DJ25 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00259_00FP | DJ25 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00259_00IV | DJ25 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00259_00IB | DJ25 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00259_00VA | DJ25 | TENSAO AZ |  |  | Measured Value
045DJGUL00259_00VB | DJ25 | TENSAO BR |  |  | Measured Value
045DJGUL00259_00VV | DJ25 | TENSAO VM |  |  | Measured Value
045DJGUL00259_0ITA | DJ25 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00259_0ITB | DJ25 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00259_0ITN | DJ25 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00259_0ITV | DJ25 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00259_0MVA | DJ25 | POT APARENTE |  |  | Measured Value
045DJGUL00259_AITA | DJ25 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00259_AITB | DJ25 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00259_AITV | DJ25 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00259_TADJ | DJ25 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00259_TFDJ | DJ25 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00259_TMDJ | DJ25 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00269_MVAR | DJ26 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00269_00MW | DJ26 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00269_00IV | DJ26 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00269_00IN | DJ26 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00269_00IB | DJ26 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00269_00IA | DJ26 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00269_00FP | DJ26 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00269_00VA | DJ26 | TENSAO AZ |  |  | Measured Value
045DJGUL00269_00VB | DJ26 | TENSAO BR |  |  | Measured Value
045DJGUL00269_00VV | DJ26 | TENSAO VM |  |  | Measured Value
045DJGUL00269_0ITA | DJ26 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00269_0ITB | DJ26 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00269_0ITN | DJ26 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00269_0ITV | DJ26 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00269_0MVA | DJ26 | POT APARENTE |  |  | Measured Value
045DJGUL00269_AITA | DJ26 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00269_AITB | DJ26 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00269_AITV | DJ26 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00269_TADJ | DJ26 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00269_TFDJ | DJ26 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00269_TMDJ | DJ26 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00309_00IN | IT30 (DJ30) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00309_00IV | IT30 (DJ30) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00309_00IB | IT30 (DJ30) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00309_00IA | IT30 (DJ30) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00319_00IA | DJ31 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00319_00FP | DJ31 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00319_MVAR | DJ31 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00319_00MW | DJ31 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00319_00IV | DJ31 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00319_00IB | DJ31 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00319_00IN | DJ31 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00319_00VA | DJ31 | TENSAO AZ |  |  | Measured Value
045DJGUL00319_00VB | DJ31 | TENSAO BR |  |  | Measured Value
045DJGUL00319_00VV | DJ31 | TENSAO VM |  |  | Measured Value
045DJGUL00319_0ITA | DJ31 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00319_0ITB | DJ31 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00319_0ITN | DJ31 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00319_0ITV | DJ31 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00319_0MVA | DJ31 | POT APARENTE |  |  | Measured Value
045DJGUL00319_AITA | DJ31 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00319_AITB | DJ31 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00319_AITV | DJ31 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00319_TADJ | DJ31 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00319_TFDJ | DJ31 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00319_TMDJ | DJ31 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00349_00IN | DJ34 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00349_00IB | DJ34 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00349_00IA | DJ34 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00349_00MW | DJ34 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00349_00FP | DJ34 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00349_00VA | DJ34 | TENSAO AZ |  |  | Measured Value
045DJGUL00349_00VB | DJ34 | TENSAO BR |  |  | Measured Value
045DJGUL00349_00VV | DJ34 | TENSAO VM |  |  | Measured Value
045DJGUL00349_0ITA | DJ34 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00349_0ITB | DJ34 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00349_0ITN | DJ34 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00349_0ITV | DJ34 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00349_0MVA | DJ34 | POT APARENTE |  |  | Measured Value
045DJGUL00349_AITA | DJ34 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00349_AITB | DJ34 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00349_AITV | DJ34 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00349_TADJ | DJ34 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00349_TFDJ | DJ34 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00349_TMDJ | DJ34 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00359_00IV | DJ35 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00359_00IN | DJ35 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00359_00IB | DJ35 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00359_00IA | DJ35 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00359_00FP | DJ35 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00359_00VA | DJ35 | TENSAO AZ |  |  | Measured Value
045DJGUL00359_00VB | DJ35 | TENSAO BR |  |  | Measured Value
045DJGUL00359_00VV | DJ35 | TENSAO VM |  |  | Measured Value
045DJGUL00359_0ITA | DJ35 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00359_0ITB | DJ35 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00359_0ITC | DJ35 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00359_0ITV | DJ35 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00359_0MVA | DJ35 | POT APARENTE |  |  | Measured Value
045DJGUL00359_AITA | DJ35 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00359_AITB | DJ35 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00359_AITV | DJ35 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00359_TADJ | DJ35 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00359_TFDJ | DJ35 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00359_TMDJ | DJ35 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00409_00IN | IT40 (DJ40) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00409_00IV | IT40 (DJ40) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00409_00IB | IT40 (DJ40) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00409_00IA | IT40 (DJ40) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00509_00IN | IT50 (DJ50) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00509_00IV | IT50 (DJ50) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00509_00IB | IT50 (DJ50) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00509_00IA | IT50 (DJ50) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGUL00609_00IV | IT60 (DJ60) | CORRENTE VM |  |  | Measured Value | Current | A | C
045DJGUL00609_00IN | IT60 (DJ60) | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00609_00IB | IT60 (DJ60) | CORRENTE BR |  |  | Measured Value | Current | A | B
045DJGUL00609_00IA | IT60 (DJ60) | CORRENTE AZ |  |  | Measured Value | Current | A | A
045DJGULSGERL_0VCC | SERV. AUX. GERAL (SAG) | TENSAO VCC |  |  | Custom | Voltage | V | Unknown
045DJGULSGERL_IBAR | SERV. AUX. GERAL (SAG) | CORRENTE CC - BARRA | N2= ELIPSE
045DJGULSGERL_TISP | SERV. AUX. GERAL (SAG) | TEMP. INTERNA SALA PAINÉIS | N2= ELIPSE
045DJGULSGERL_UMRS | SERV. AUX. GERAL (SAG) | UMIDADE RELATIVA SALA PAINÉIS | N2= ELIPSE
045SAGUL00019_00VV | SERV. AUX. 1 (SAX1) | TENSAO VM |  |  | Measured Value | Voltage | V | C
045SAGUL00019_00VB | SERV. AUX. 1 (SAX1) | TENSAO BR |  |  | Measured Value | Voltage | V | B
045SAGUL00019_00VA | SERV. AUX. 1 (SAX1) | TENSAO AZ |  |  | Measured Value | Voltage | V | A
045SAGUL00019_00IA | SERV. AUX. 1 (SAX1) | CORRENTE AZ |  |  | Measured Value
045SAGUL00019_00IB | SERV. AUX. 1 (SAX1) | CORRENTE BR |  |  | Measured Value
045SAGUL00019_00IV | SERV. AUX. 1 (SAX1) | CORRENTE VM |  |  | Measured Value
045SAGUL00019_00MW | SERV. AUX. 1 (SAX1) | POT ATIVA |  |  | Measured Value
045SAGUL00019_MWHE | SERV. AUX. 1 (SAX1) | ENERGIA ATIVA ENTREGUE |  |  | Measured Value
045SAGUL00019_MVAR | SERV. AUX. 1 (SAX1) | POT REATIVA |  |  | Measured Value
045SAGUL00019_00FP | SERV. AUX. 1 (SAX1) | FATOR DE POTENCIA |  |  | Measured Value
045SAGUL00019_MRHE | SERV. AUX. 1 (SAX1) | ENERGIA REATIVA ENTREGUE |  |  | Measured Value
045SAGUL00019_0VCC | RET1 | TENSÃO VCC RET 1 | N2= ELIPSE
045SAGUL00019_0ICC | RET1 | CORRENTE CC RET 1 | N2= ELIPSE
045SAGUL00029_00VB | SERV. AUX. 2 (SAX2) | TENSAO BR |  |  | Measured Value | Voltage | V | B
045SAGUL00029_00VV | SERV. AUX. 2 (SAX2) | TENSAO VM |  |  | Measured Value | Voltage | V | C
045SAGUL00029_00VA | SERV. AUX. 2 (SAX2) | TENSAO AZ |  |  | Measured Value | Voltage | V | A
045SAGUL00029_00IA | SERV. AUX. 2 (SAX2) | CORRENTE AZ |  |  | Measured Value
045SAGUL00029_00IB | SERV. AUX. 2 (SAX2) | CORRENTE BR |  |  | Measured Value
045SAGUL00029_00IV | SERV. AUX. 2 (SAX2) | CORRENTE VM |  |  | Measured Value
045SAGUL00029_00MW | SERV. AUX. 2 (SAX2) | POT ATIVA |  |  | Measured Value
045SAGUL00029_MWHE | SERV. AUX. 2 (SAX2) | ENERGIA ATIVA ENTREGUE |  |  | Measured Value
045SAGUL00029_MVAR | SERV. AUX. 2 (SAX2) | POT REATIVA |  |  | Measured Value
045SAGUL00029_00FP | SERV. AUX. 2 (SAX2) | FATOR DE POTENCIA |  |  | Measured Value
045SAGUL00029_MRHE | SERV. AUX. 2 (SAX2) | ENERGIA REATIVA ENTREGUE |  |  | Measured Value
045SAGUL00039_00VB | SC11 (DJ03) | TENSAO BR |  |  | Measured Value | Voltage | V | B
045SAGUL00039_00VV | SC11 (DJ03) | TENSAO VM |  |  | Measured Value | Voltage | V | C
045SAGUL00039_00VA | SC11 (DJ03) | TENSAO AZ |  |  | Measured Value | Voltage | V | A
045SAGUL00039_00IA | SC11 (DJ03) | CORRENTE AZ |  |  | Measured Value
045SAGUL00039_00IB | SC11 (DJ03) | CORRENTE BR |  |  | Measured Value
045SAGUL00039_00IV | SC11 (DJ03) | CORRENTE VM |  |  | Measured Value
045SAGUL00039_00MW | SC11 (DJ03) | POT ATIVA |  |  | Measured Value
045SAGUL00039_MWHE | SC11 (DJ03) | ENERGIA ATIVA ENTREGUE |  |  | Measured Value
045SAGUL00039_MVAR | SC11 (DJ03) | POT REATIVA |  |  | Measured Value
045SAGUL00039_00FP | SC11 (DJ03) | FATOR DE POTENCIA |  |  | Measured Value
045SAGUL00039_MRHE | SC11 (DJ03) | ENERGIA REATIVA ENTREGUE |  |  | Measured Value
045TRGUL00029_COPR | TR02 | CONTADOR OPERACOES COMUTADOR | N2= ELIPSE
045TRGUL00039_049A | TR03 | TEMP ENROL |  |  | Measured Value | Temperature | C | Unknown
045TRGUL00039_0026 | TR03 | TEMP OLEO |  |  | Measured Value | Temperature | C | Unknown
045TRGUL00039_0TAP | TR03 | POSIÇÃO DO TAP |  |  | Measured Value
045TRGUL00039_COPR | TR03 | CONTADOR OPERACOES COMUTADOR | N2= ELIPSE
045TRGUL00049_049A | TR04 | TEMP ENROL |  |  | Measured Value | Temperature | C | Unknown
045TRGUL00049_0026 | TR04 | TEMP OLEO |  |  | Measured Value | Temperature | C | Unknown
045TRGUL00049_0TAP | TR04 | POSIÇÃO DO TAP |  |  | Measured Value
045TRGUL00049_COPR | TR04 | CONTADOR OPERACOES COMUTADOR | N2= ELIPSE
045DJGUL00329_00FP | DJ32 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00329_MVAR | DJ32 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00329_00MW | DJ32 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00329_00IV | DJ32 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00329_00IB | DJ32 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00329_00IN | DJ32 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00329_00VA | DJ32 | TENSAO AZ |  |  | Measured Value
045DJGUL00329_00VB | DJ32 | TENSAO BR |  |  | Measured Value
045DJGUL00329_00VV | DJ32 | TENSAO VM |  |  | Measured Value
045DJGUL00329_0ITA | DJ32 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00329_0ITB | DJ32 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00329_0ITN | DJ32 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00329_0ITV | DJ32 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00329_0MVA | DJ32 | POT APARENTE |  |  | Measured Value
045DJGUL00329_AITA | DJ32 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00329_AITB | DJ32 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00329_AITV | DJ32 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00329_TADJ | DJ32 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00329_TFDJ | DJ32 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00329_TMDJ | DJ32 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00339_00IA | DJ33 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00339_00FP | DJ33 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00339_MVAR | DJ33 | POT REATIVA |  |  | Measured Value | Reactive Power | MVAr | ABC
045DJGUL00339_00MW | DJ33 | POT ATIVA |  |  | Measured Value | Active Power | MW | ABC
045DJGUL00339_00IV | DJ33 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00339_00IB | DJ33 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045DJGUL00339_00IN | DJ33 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00339_00VA | DJ33 | TENSAO AZ |  |  | Measured Value
045DJGUL00339_00VB | DJ33 | TENSAO BR |  |  | Measured Value
045DJGUL00339_00VV | DJ33 | TENSAO VM |  |  | Measured Value
045DJGUL00339_0ITA | DJ33 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00339_0ITB | DJ33 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00339_0ITN | DJ33 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00339_0ITV | DJ33 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00339_0MVA | DJ33 | POT APARENTE |  |  | Measured Value
045DJGUL00339_AITA | DJ33 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00339_AITB | DJ33 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00339_AITV | DJ33 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00339_TADJ | DJ33 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00339_TFDJ | DJ33 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00339_TMDJ | DJ33 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00359_MVAR | DJ35 | POT REATIVA |  |  | Measured Value
045DJGUL00359_00MW | DJ35 | POT ATIVA |  |  | Measured Value
045SAGUL00029_0VCC | RET2 | TENSÃO VCC RET 2 | N2= ELIPSE
045SAGUL00029_0ICC | RET2 | CORRENTE CC RET 2 | N2= ELIPSE
045DJGUL00369_00IA | DJ36 | CORRENTE AZ | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00369_00IV | DJ36 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | C
045DJGUL00369_00IB | DJ36 | CORRENTE BR | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | B
045TRGUL00019_0TAP | TR01 | POSIÇÃO DO TAP |  |  | Measured Value
045TRGUL00029_0TAP | TR02 | POSIÇÃO DO TAP |  |  | Measured Value
045TRGUL00029_049A | TR02 | TEMP ENROL |  |  | Measured Value | Temperature | C | Unknown
045TRGUL00029_0026 | TR02 | TEMP OLEO |  |  | Measured Value | Temperature | C | Unknown
045TRGUL00019_049A | TR01 | TEMP ENROL |  |  | Measured Value | Temperature | C | Unknown
045TRGUL00019_0026 | TR01 | TEMP OLEO |  |  | Measured Value | Temperature | C | Unknown
045TRGUL00019_COPR | TR01 | CONTADOR OPERACOES COMUTADOR | N2= ELIPSE
045TRGUL00029_COPR | TR02 | CONTADOR OPERACOES COMUTADOR | N2= ELIPSE
045DJGUL00349_00IV | DJ34 | CORRENTE VM | EQ. ELIPSE SINAL (-) |  | Measured Value | Current | A | A
045DJGUL00369_00IN | DJ36 | CORRENTE NE |  |  | Measured Value | Current | A | N
045DJGUL00369_00FP | DJ36 | FATOR DE POTENCIA |  |  | Measured Value | Power Factor | Default | ABC
045DJGUL00369_00VA | DJ36 | TENSAO AZ |  |  | Measured Value
045DJGUL00369_00VB | DJ36 | TENSAO BR |  |  | Measured Value
045DJGUL00369_00VV | DJ36 | TENSAO VM |  |  | Measured Value
045DJGUL00369_0ITA | DJ36 | CORRENTE DE TRIP AZ |  |  | Measured Value
045DJGUL00369_0ITB | DJ36 | CORRENTE DE TRIP BR |  |  | Measured Value
045DJGUL00369_0ITC | DJ36 | CORRENTE DE TRIP N |  |  | Measured Value
045DJGUL00369_0ITV | DJ36 | CORRENTE DE TRIP VM |  |  | Measured Value
045DJGUL00369_0MVA | DJ36 | POT APARENTE |  |  | Measured Value
045DJGUL00369_AITA | DJ36 | CORRENTE ACUMULADA TRIP AZ | N2= ELIPSE |  | Measured Value
045DJGUL00369_AITB | DJ36 | CORRENTE ACUMULADA TRIP BR | N2= ELIPSE |  | Measured Value
045DJGUL00369_AITV | DJ36 | CORRENTE ACUMULADA TRIP VM | N2= ELIPSE |  | Measured Value
045DJGUL00369_TADJ | DJ36 | TEMPO DE ABERTURA DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00369_TFDJ | DJ36 | TEMPO DE FECHAMENTO DISJ | N2= ELIPSE |  | Measured Value
045DJGUL00369_TMDJ | DJ36 | TEMPO CARREGAMENTO MOLA | N2= ELIPSE |  | Measured Value
045DJGUL00369_MVAR | DJ36 | POT REATIVA |  |  | Measured Value
045DJGUL00369_00MW | DJ36 | POT ATIVA |  |  | Measured Value
045DJGUL00329_00IN | DJ32 | CORRENTE NE |  |  | Measured Value |  | A
045DJGUL00349_MVAR | DJ34 | POT REATIVA |  |  | Measured Value